## Home
Chapter 2: Heat Exchangers
Rules of Thumb for Chemical Engineers, 5th Edition
by Stephen Hall
Units:
This Excel workbook includes Visual Basic for Application function subroutines.
Macros must be enabled for them to work.
Guide to Using this Workbook
The primary purpose of this workbook is to demonstrate the use of the Bell-Delaware method for rating shell-and-tube heat exchangers. The method is applicable to exchangers with NO PHASE change. The worksheets follow the text in the stepwise evaluation of a heat transfer problem that is defined by the hot and cold fluid properties. Input cells have RED text. Cells with black text are formulas.
1. Define the components in the hot and cold streams on the Process Fluids worksheet. Store the properties for new (previously unknown) components on the Fluid Data worksheet.
2. Define the mass fraction of the components, flow rates, and temperatures on the Process Data worksheet
3. Use the Tubes Pressure Drop worksheet to determine the tube diameter, length and number of tube passes in the exchanger, based on a pressure drop criteria
4. Calculate the inside film coefficient on the Tubes htc worksheet
5. Determine the shell diameter and enter information about the tube bundle and baffles on the Shell Geometry worksheet.
6. Calculate the outside film coefficient on the Shell htc worksheet
7. Determine the pressure drop on the shell side on the Shell Pressure Drop worksheet
8. Compute the overall heat transfer coefficient, clean and fouled, on the Overall U worksheet; iterate until the assumed overall U in Step 3 agrees with the calculated U-clean
9. Complete a TEMA datasheet on the Shell-and-Tube worksheet
10. The Conversions worksheet is used for data, including the status of radio buttons and checkboxes, and must not be deleted!
ChemEng Software sells an Excel template called TANKJKT
www.chemengsoftware.com
TANKJKT models heat transfer in vessels with jackets and/or internal coils. It includes a database of properties for glass-lined reactors, heat transfer fluids, and insulation materials. Order on-line or by telephone, 24-h/d; credit cards accepted.

## Process Fluids
Use this worksheet to define the components present in the hot and cold streams for a heat transfer problem.
Multiple components from the Fluid Data properties table can be specified, and their properties will be averaged.
Averging properties for non-ideal solutions, such as polar mixtures (with water), gives poor results.
A better approach is to define the properties for the mixtures at several temperatures and add them to the database.
The composition (i.e., mass fraction of each component) is specifed on the next worksheet.
Use the dropdown list to view the Fluid Data content: |  |  | Methyl Alcohol
To add new materials to the Fluid Data, go to the Fluid Data worksheet tab
Hot Fluid Components
| Name | in Data Table? | Description
1 | Water | YES | City water
2 | Methyl Alcohol | YES | pure component
3
4
5
6
7
8
9
Cold Fluid Components
| Name | in Data Table? | Description
1 | Water | YES | City water
2
3
4
5
6
7
8
9
Problem Statement: Define components for the hot and cold streams

## Process Data
Inputs
Hot Side
| Fluid name |  | Distilled Water
| Flow Total | lb/h | 396000
| Temperature, in | °F | 89.6 | [11 empty] | Temp, C | 32
| Temperature, out | °F | 77 | [11 empty] | Temp, C | 25 | Heat | -5002748.416 | Btu/h | -1466305.5607 | Watts
| Pressure, in | psig | 29.0075
| Press Drop Allowed | psig | 1.5
| Fouling Resistance | ft²-h-°F/Btu | 0.00049969 |  |  |  | Heat Transferred
[7 empty] | 5002748.416 | Btu/h
Cold Side
| Fluid name |  | Raw Water
| Flow Total | lb/h | 1188000
| Temperature, in | °F | 68 | [11 empty] | Temp, C | 20
| Temperature, out | °F | 72.2012 | [11 empty] | Temp, C | 22.334 | Heat | 5002748.416 | Btu/h | 1466305.5607 | Watts
| Pressure, in | psig | 60
| Press Drop Allowed | psig | 10 | [14 empty] | -1.872e-07
| Fouling Resistance | ft²-h-°F/Btu | 0.00049969
[6 empty] | mass frac | [5 empty] | mass frac | [13 empty] | Viscosity Based on the Wall Temperatures
|  |  |  | Component |  | Density | Viscosity |  | Sp Heat | Therm Cond | H Vap | Density | Viscosity |  | Sp Heat | Therm Cond | Antoine Coefficients |  |  | VP | VP | Partial P |  | Viscosity using Eq 27-3 |  | If Shell Side |  | If Tube Side
| Hot Side Fluid Components |  |  | mass fraction | mole fraction | lb/ft3 | cP | MW | Btu/lb-°F | Btu/h-ft-°F | Btu/lb | lb/ft3 | cP | MW | Btu/lb-°F | Btu/h-ft-°F | A | B | C | mm Hg | psig | psig |  | Wi ln(visc) |  | cP | ln(cP) | cP | ln(cP)
1 | Water |  |  | 1 |  | 61.9091 | 0.77409 | 18.02 | 1.0028 | 0.35043 | 971.6251 | 62.1093 | 0.9025 | 18.02 | 1.0025 | 0.34568 | 8.0276 | 1706.1342 | 231.4922 | 35.6911 | -14.0058 |  | 1 | -0.25606 | -0.10259 | 0.94347 | -0.058191 | 0.92645 | -0.076395
2 | Methyl Alcohol |  |  | 0 |  | 0 | 0.51586 | 32.04 | 0 | 0 | 472.9149 | 0 | 0.5624 | 32.04 | 0 | 0 | 7.9749 | 1515.293 | 232.9925 | 180.5742 | -11.2043 |  | 0 | 0 | 0 | 0.57632 | 0 | 0.57059 | 0
3
4
5
6
7
8
9
|  |  |  | OK |  | 61.9091 | 0.77409 |  | 1.0028 | 0.35043 |  | 62.1093 | 0.9025 |  | 1.0025 | 0.34568 | [7 empty] | -0.25606 | -0.10259 | 0.94347 | -0.058191 | 0.92645 | -0.076395
Cold Side Fluid Components
1 | Water |  |  | 1 |  | 62.2523 | 1.016 | 18.02 | 1.0023 | 0.34229 | 971.6251 | 62.1855 | 0.9604 | 18.02 | 1.0024 | 0.34387 | 8.0276 | 1706.1342 | 231.4922 | 35.6911 | -14.0058 |  | 1 | 0.015857 | -0.040408 | 0.94347 | -0.058191 | 0.92645 | -0.076395
2
3
4
5
6
7
8
9
|  |  |  | OK |  | 62.2523 | 1.016 |  | 1.0023 | 0.34229 |  | 62.1855 | 0.9604 |  | 1.0024 | 0.34387 | [7 empty] | 0.015857 | -0.040408 | 0.94347 | -0.058191 | 0.92645 | -0.076395
|  |  | Shell Side |  |  | Tube Side
| Parameter | Units | In | Out |  | In | Out
| Fluid Name |  | Distilled Water |  |  | Raw Water
| Flow Total | lb/h | 396000 |  |  | 1188000
| Vapor | lb/h
| Liquid | lb/h
| Steam | lb/h
| Water | lb/h
| Noncondensable | lb/h
| Evap/Cond | lb/h
| Temperature (In/Out) | °F | 89.6 |  |  | 68
| Density | lb/ft3
| Viscosity | cP
Molecular Weight, vapor
Molecular Weight, noncondensibles
| Specific Heat | Btu/lb-°F
| Thermal Conductivity | Btu/h-ft-°F
| Latent Heat | Btu/lb
| Inlet Pressure | psig | 29.0075 |  |  | 60
| Velocity | ft/s
| Press Drop Allowed | psig | 1.5 |  |  | 10
| Fouling Resistance | ft²-h-°F/Btu | 0.00049969 |  |  | 0.00049969
Problem Statement: Specify process conditions for a liquid-liquid heat exchange problem, and perform a heat balance

## Tubes Pressure Drop
Inputs
| Fluid flowing in tubes |  | Raw Water
| Assumed overall U | Btu/h-ft²-°F | 520
| Safety factor for fouling |  | 20%
| Tube OD | in | 0.75
| Tube wall thickness | BWG | 14
| Tube length | ft | 15
| Tube Passes |  | 1
| Shell Passes |  | 1
Data (from the Process Data and F Factor worksheets)
| Flow rate | lb/h | 1188000
| Heat transferred | Btu/h | 5002748.416
| Temp diff correction factor |  | 1
| Average viscosity | cP | 0.98819
| Average density | lb/ft3 | 62.2189
| Pressure at inlet | psig | 60
| Pressure drop allowed | psig | 10
| Tube roughness | ft | 6.7e-06
Calculations
| Tube inside diameter | in | 0.584
| Flow area per tube | ft² | 0.0018602
| Tube area available | ft²/ft | 0.19635
| Log-mean temp diff | °F | 12.7413
| Mean temperature difference | °F | 12.7413
| Adjusted duty | Btu/h | 6003298.0991
| Tube area required | ft² | 906.091
| Total tube length req | ft | 4614.6837
| Number of tubes |  | 308
| Tubes per pass |  | 308
| Actual area | ft² | 907.1349
| Flow rate per tube | lb/h | 3857.1429
| Velocity in tube | ft/s | 9.2574
| Reynolds Number |  | 42215.0943
| Friction Factor |  | 0.022095
| Pressure Drop, tubes | psig | 3.9189
| Pressure drop, enter/exit | ft fluid | neglect
| Enter/exit tubes | ft fluid | 1.9961
| End losses in bonnets/channels | ft fluid | 0
| Subtotal, extra losses tube side | ft fluid | 1.9961
|  | psig | 0.86246
| Total pressure drop, tube side | psig | 4.7813
Note on D12: Standard tube lengths in the US are 4, 8, 12, 15, and 20 ft
Note on D13: Minimum = number of shell passes, or may be a multiple of 2 times the shell passes. This is the total number of tube passes, example: 3 shells, 2 tube passes in each shell = 6 tube passes
Note on D40: Typical value is 0.5 to 2.5 m/s or 2 to 8 ft/s
Note on D8: After stepping through all of the worksheets to "Overall U", come back here and iterate this assumption until it agrees with the calculated (clean) U
Problem Statement: Calculate the tube side pressure drop based on process data and heat load, using rule-of-thumb heat transfer rate and safety factor
Result

## F Factor
Inputs (copied from the Process Data and Tubes worksheets)
Hot Side
| Fluid name |  | Distilled Water
| Temperature, in | °F | 89.6
| Temperature, out | °F | 77
Cold Side
| Fluid name |  | Raw Water
| Temperature, in | °F | 68
| Temperature, out | °F | 72.2012
| Tube passes |  | 1
| Shell passes | N | 1
Calculations
| Intermediate value | R | 2.9991
| Intermediate value | P | 0.1945
| Intermediate value | S | 1.5814
| Intermediate value | W | 0.51728
| Intermediate value | W' | 0.8055
General Case
| Numerator |  | -1.0424
| Denomenator |  | -1.107
| General Case Answer | F | 0.9417
R=1 Case
| Numerator |  | 0.34149
| Denomenator |  | 0.34487
| R=1 Answer | F | 0.99021
| Choose which one | F | 0.9417
Problem Statement: Calculate the LMTD configuration correction factor
Result

## Tubes htc
Inputs | Fluid flowing in tubes |  | Raw Water
| Assumed inside heat transfer coef | Btu/h-ft²-°F | 1056.6612
Data (from the Process Data and Tubes Pressure Drop worksheets)
| Assumed overall U | Btu/h-ft²-°F | 520
| Outside surface area | ft² | 907.1349
| Tube outside diameter | in | 0.75
| Tube inside diameter | in | 0.584
|  | ft | 0.048667
| Tube length (one path) | ft | 4620
| Bulk viscosity | cP | 0.98819
| Viscosity at tube wall | cP | 0.92645
| Bulk heat capacity | Btu/lb-°F | 1.0023
| Bulk thermal conductivity | Btu/h-ft-°F | 0.34308
| Reynolds Number |  | 42215.0943
Calculations
| Inside surface area | ft² | 706.3557
| Overall U based on inside area | Btu/h-ft²-°F | 667.8082
| Average temperature, shell side | °F | 70.1006
| Average temperature, tube side | °F | 83.3
| Mean wall temperature, inside | °F | 74.958
|  | Temp, C | 23.8656
| Sieder-Tate term (visc ratio^0.14) |  | 1.0091
| Prandl Number |  | 6.9839
Laminar flow calculation
| Inside heat transfer coefficient | Btu/h-ft²-°F | 26.8326
Turbulent flow calculation
| Inside heat transfer coefficient | Btu/h-ft²-°F | 1568.7451
Transition flow calculation
| Inside heat transfer coefficient | Btu/h-ft²-°F | 7777.8521
Choose which one
| Inside heat transfer coefficient | Btu/h-ft²-°F | 1568.7451
Problem Statement: Calculate the tube side heat transfer coefficient
Result

## Shell Geometry
Inputs
| Number of shells |  | 1
| Shell inside diameter | in | 21.25 | <-- Minimum diameter is 23.3 in
| Outer tube limit (diameter) | in | 19
| Baffle cut | fraction | 0.25
| Baffle spacing | in | 10
| Baffle diameter | in | 21
| Number of sealing strips per side |  | 2
| Tube pitch layout |  | 90
| Tube pitch ratio |  | 1.33
Data (from Tubes Pressure Drop worksheet)
| Number of tubes in the exchanger | N | 308
| Outside diameter of tubes | in | 0.75
| Tube length | ft | 15
| Tube passes |  | 1
Calculations
| Tube pitch | in | 0.9975
| Longitudinal Tube Pitch | in | 0.9975
| Cross section for 1 tube equivalent | in2 | 0.99501
| Cross section for all tubes | in2 | 306.4619
| Area corrected for tube passes | in2 | 306.4619
| Minimum calculated shell diameter | in | 21.2535
| Standard diameter from table | in | 23.25
| Approximate max unsupported tube span | in | 59.6386
| Number of effective crossflow rows in each window |  | 4.2607
| Number of baffles |  | 16
Note on D11: Minimum baffle spacing is generally one-fifth of the shell diameter and not less than 2 inches. Maximum spacing is limited by the maximum unsupported tube span (in inches, equals 74 d^.75), divided by 2, reduced by 12% for Al, Cu, and their alloys. Optimum baffle spacing is between 0.4 and 0.6 of the shell diameter
Note on D9: Typically, the outer tube limit is (shell diameter - 26) mm for shells 635 mm (25 in) and larger; (shell diameter - 22 mm) for shells that are 254 to 610 mm (10 to 24 in) and slightly less for smaller shells
Problem Statement: Calculate the shell side geometrical parameters

## Shell htc
Inputs | Fluid flowing in shell |  | Distilled Water
| Assumed outside heat transfer coef | Btu/h-ft²-°F | 704.4408
| Baffle hole clearance |  | 0.03125
Data
| Flow rate | lb/h | 396000
|  | lb/s | 110
| Assumed overall U | Btu/h-ft²-°F | 520
| Outside surface area | ft² | 907.1349
| Tube outside diameter | in | 0.75
|  | ft | 0.0625
| Number of tubes in the exchanger | N | 308
| Viscosity at tube wall | cP | 0.92645
| Bulk viscosity, shell | cP | 0.8383
|  | lb/ft-s | 0.00056329
| Wall viscosity, shell | cP | 0.94347
| Bulk heat capacity, shell | Btu/lb-°F | 1.0026
| Bulk thermal conductivity, shell | Btu/h-ft-°F | 0.34806
|  | Btu/s-ft-F | 9.6683e-05
| Shell inside diameter | in | 21.25
| Tube bundle outside diameter | in | 19
| Baffle cut fraction |  | 0.25
| Baffle spacing | in | 10
| Pitch layout |  | 90
| Pitch Ratio |  | 1.33
| Tube Pitch | in | 0.9975
| Tube Pitch, normal to flow | in | 0.9975
| Tube Pitch, parallel to flow | in | 0.9975
| Number of sealing strip pairs per side |  | 2
Calculations
| Average temperature, shell side | °F | 70.1006
| Average temperature, tube side | °F | 83.3
| Mean wall temperature, outside | °F | 73.5566
|  | Temp, C | 23.087
| Crossflow area between baffles, As | ft² | 0.47071
| Reynolds Number |  | 25929.2865
| j-ideal factor coefficients | a1 | 0.37
|  | a2 | -0.395
|  | a3 | 1.187
|  | a4 | 0.37
|  | a | 0.16921
| j-ideal factor |  | 0.0066797
| Sieder-Tate term (visc ratio^0.14) |  | 0.98359 |  | Overall losses |  | 0.69227
| Ideal heat transfer coefficient | Btu/h-ft²-°F | 1708.5919 |  | Outside heat transfer coefficient | Btu/h-ft²-°F | 1182.8063 | 6741.9958
Correction Factor for Baffle Cut and Spacing
| Baffle cut, lc | in | 5.3125
| Intermediate |  | 0.55921
| Fraction of tubes in crossflow | Fc | 0.67293
| Baffle cut correction factor | Jc | 1.0345
Correction Factor for Baffle Leakage Effects
| Angle to edge of baffle | Theta-1 | 1.0472 | 2.0944
| Shell-to-baffle spacing | sb | 0.25
| Shell-to-baffle leakage area | Asb | 5.5632
| Shell-to-outer tube limit distance | C1 | 2.25 | 18.25
| Angle to edge of tubes and baffle | Theta-3 | 1.9547 | 1.8987
| Fraction of tubes in one window | Fw | 0.16354 | 0.15152
| Baffle hole to tube OD spacing | tb | 0.03125
| Tube-to-baffle leakage area | Atb | 4.7424
| Angle to window | Theta-2 | 2.0409 | 2.0944
| Tubes in baffle window | Ntw | 50 | 46.669
| Area occupied by tubes in window | Awt | 22.0893 | 20.6177
| Gross window area | Awg | 64.8736 | 69.3357
| Free area for fluid flow in one window | Aw | 42.7843 | 48.718 | Equiv Diam | 0.22926
| Intermediate | ra | 0.53982
| Intermediate | rb | 0.24087
| Baffle Leakage Effects factor | Jl | 0.77921
Correction Factor for Bundle and Partition Bypass Effects
| Formula coefficient | C | 1.25
| Number of bypass divider lanes | Np | 0
| Width of bypass divider lanes | wp | 1.5
| Area of bypass divider lanes, Abp | ft² | 0.15625
| Ratio, bypass to crossflow area | rc | 0.33195
| Tube crossings | Ncc | 10.6516
| Ratio of sealing strips to tubes |  | 0.18776
| Bundle Bypass Factor | Jb | 0.89085
Correction for Variations in Baffle Spacing
Assuming even number of baffles so shell nozzles are on opposite sides
Odd number of flow lanes
Assume equal spacing for inlet and outlet baffles
| Number of baffles |  | 16
| Length of center section, baffled | in | 150
| Inlet and Outlet baffle spacing | in | 15
| Exponent | n | 0.6
| Li* |  | 1.5
| Lo* |  | 1.5
| Baffle Spacing Factor | Js | 0.96401
Correction for Temperature Gradient if Laminar Flow
| Number of tube rows in one crossflow section |  | 10.6516
| Correction factor |  | 1
Problem Statement: Calculate the shell side film coefficient using the Bell-Delaware method

## Shell Pressure Drop
Inputs
Data (from Shell htc worksheet)
| Reynolds Number |  | 25929.2865
| Number of baffles |  | 16
| Pitch Ratio |  | 1.33
| Tube Pitch | in | 0.9975
| Tube Outside Diameter | in | 0.75
| Sieder-Tate term (visc ratio^0.14) |  | 0.98359
| Flow rate | lb/s | 110
| Tubes in one crossflow section | Nr,cc | 10.6516
| Tube crossings in window | Nr,tw | 3.0576
| Density | lb/ft3 | 62.0092
| Conversion factor | gc | 32.17
| Flow area, crossflow section, As | ft² | 0.47071
| Flow area, window, Aw | ft² | 0.29711
| Ratio, bypass to crossflow area | rc | 0.33195
| Ratio of sealing strips to tubes |  | 0.18776
| Intermediate | ra | 0.53982
| Intermediate | rb | 0.24087
| Baffle spacing, center |  | 10
| Baffle spacing, inlet zone |  | 15
| Baffle spacing, outlet zone |  | 15
Calculations
Velocity in crossflow at widest diameter
| Velocity | ft/s | 3.7686
Ideal Pressure Drop per Crossflow Section
| f-ideal factor coefficients | b1 | 0.391
|  | b2 | -0.148
|  | b3 | 6.3
|  | b4 | 0.378
|  | b | 0.83728
| f-ideal factor |  | 0.086883
| Pressure Drop, one crossflow section | psig | 0.3461
| Crossflow pressure drop, ideal | psig | 5.1916
Bypass correction factor
| Coefficient | Cbp | 3.7
| Bypass correction factor | RB | 0.71028
Leakage correction factor
| Intermediate exponent |  | 0.56903
| Leakage correction factor | RL | 0.4021
| Crossflow pressure drop, corrected | psig | 1.4827
Window Pressure Drop
| Average flow per window | mw | 294.1414
| Equivalent diameter of baffle window | ft | 0.10291
| Window pressure drop | psig | 2.0297
End Zones Pressure Drop
| Exponent |  | 0.2
| Correction factor, baffle spacing | RS | 0.96397
| End zones pressure drop | psig | 0.0021181
| TOTAL Shell Side Pressure Drop | psig | 3.5146
Problem Statement: Calculate the shell side pressure drop

## Overall U
Inputs
| Material of construction, tubes |  | Cr-alloy (0.5% Cr)
Data
| Assumed U | Btu/h-ft²-°F | 520
| Film coefficient, tubes | Btu/h-ft²-°F | 1568.7451
| Fouling resistance, tubes |  | 0.00049969
| Fouling resistance, shell |  | 0.00049969
| Film coefficient, shell | Btu/h-ft²-°F | 1182.8063
| Outside diameter, tubes | in | 0.75
| Inside diameter, tubes | in | 0.584
| Thermal conductivity, tubes | Btu/h-ft-°F | 24
| Heat transferred | Btu/h | 5002748.416
| Mean temperature difference | °F | 12.7413
Calculations
| Overall U, calculated, clean | Btu/h-ft²-°F | 502.5535
| Overall U, calculated, dirty | Btu/h-ft²-°F | 319.3616
| Area required, clean | ft² | 781.2888
| Area required, fouled | ft² | 1229.4509
| Area provided by the design | ft² | 907.1349
| Oversurface |  | 16.11%
Problem Statement: Calculate the overall heat transfer coefficient and compare with the assumed value

## Nozzles
Inputs
| Max Velocity, tubeside nozzles | ft/s | 5
| Max Velocity, shellside nozzles | ft/s | 3
Data
Tubeside
| Flow rate | lb/h | 1188000
| Inlet density | lb/ft3 | 62.2523
| Outlet density | lb/ft3 | 62.1855
Shellside
| Flow rate | lb/h | 396000
| Inlet density | lb/ft3 | 61.9091
| Outlet density | lb/ft3 | 62.1093
Calculations
Tubeside
| Volumetric flow rate, tubeside inlet | ft3/s | 5.301
| Minimum ID of nozzle | in | 13.9422
| Selected nozzle | in | 15.624
| Selected nozzle designation | in | 16
| Velocity | ft/s | 3.9815
| rho-v2 | lb/ft2-s | 986.8449
| Weight | lb | 146
| Volumetric flow rate, tubeside outlet | ft3/s | 5.3067
| Minimum ID of nozzle | in | 13.9497
| Selected nozzle | in | 15.624
| Selected nozzle designation | in | 16
| Velocity | ft/s | 3.9858
| rho-v2 | lb/ft2-s | 987.904
| Weight | lb | 146
Shellside
| Volumetric flow rate, shellside inlet | ft3/s | 1.7768
| Minimum ID of nozzle | in | 10.4206
| Selected nozzle | in | 12.39
| Selected nozzle designation | in | 12
| Velocity | ft/s | 2.1221
| rho-v2 | lb/ft2-s | 278.7986
| Weight | lb | 90
| Volumetric flow rate, shellside outlet | ft3/s | 1.7711
| Minimum ID of nozzle | in | 10.4038
| Selected nozzle | in | 12.39
| Selected nozzle designation | in | 12
| Velocity | ft/s | 2.1153
| rho-v2 | lb/ft2-s | 277.9001
| Weight | lb | 90
Problem Statement: Specify the size of the nozzles

## Weight
Inputs
| Tubesheet thickness | in | 1
| Baffle Thickness | in | 0.5
Data
| Shell Inside Diameter | ft | 1.7708
| Shell Thickness | ft | 0.0625
| Shell Length | ft | 15
| Number of Baffles |  | 16
| Tube Outside Diameter | ft | 0.0625
| Tube Inside Diameter | ft | 0.048667
| Number of Tubes |  | 308
| Weight of steel | lb/ft3 | 489.5
| Density of water | lb/ft3 | 62.4
Calculations
| Shell metal volume | ft3 | 2.6538
| Shell weight | lb | 1299.0286
| Add for heads | lb | 456.2313
| Add for four flanges | lb | 720
| Add for nozzles | lb | 180
| Total, Shell | lb | 2788.0229
| Tube volume (inside the tubes) | ft3 | 8.594
| Tube volume (outside the tubes) | ft3 | 14.174
| Tube Weight | lb | 2731.4042
| Tubesheet | lb | 200.9309 | assumes two tubesheets
| Add for nozzles | lb | 292
| Baffles | lb | 803.7236
| Total, Tube Bundle empty | lb | 4229.4616
| Total Weight, empty | lb | 7017.4845
| Shell inside volume | ft3 | 36.9434
| Heads volume | ft3 | 3.6943
| Less volume of tube metal | ft3 | -5.58
| Weight of Water filling the void | lb | 2187.6017
| Total Weight, full of water | lb | 9205.0862
Problem Statement: Estimate the weight of the heat exchanger

## Shell-and-Tube
SHELL-AND-TUBE HEAT EXCHANGER
[7 empty] | CLIENT |  | EQUIP. NO |  | PAGE
REV | PREPARED BY |  | DATE |  | APPROVAL |  | W.O. |  | REQUISITION NO. |  | SPECIFICATION NO.
0
1 | [6 empty] | UNIT | AREA | PROCURED BY |  | INSTALLED BY
2
1 | Size |  |  | TEMA Type |  |  |  | Connected in (series/parallel)
2 | Surface per Unit |  |  | 907.1349 |  | Shells per Unit |  | 1 | Surface per Shell |  | 907.1349 | ft²
3 | Performance of One Unit
4 | Fluid Allocation | [5 empty] | Shell Side |  |  | Tube Side
6 | Fluid Name | [5 empty] | Distilled Water |  |  | Raw Water
7 | Flow Total |  |  | lb/h |  |  | 396000 |  |  | 1188000
8 | Vapor |  |  | lb/h | (in/out)
9 | Liquid |  |  | lb/h | (in/out) |  | 396000 |  |  | 1188000
10 | Steam |  |  | lb/h | (in/out)
11 | Water |  |  | lb/h | (in/out)
12 | Noncondensable |  |  | lb/h | (in/out)
13 | Temperature (In/Out) |  |  | °F | (in/out) |  | 89.6 | 77 |  | 68 | 72.2012
14 | Density |  |  | lb/ft3 |  |  | 61.9091 | 62.1093 |  | 62.2523 | 62.1855
15 | Viscosity |  |  | cP |  |  | 0.77409 | 0.9025 |  | 1.016 | 0.9604
16 | Molecular Weight, vapor
17 | Specific Heat |  |  | Btu/lb-°F |  |  | 1.0028 | 1.0025 |  | 1.0023 | 1.0024
18 | Thermal Conductivity |  |  | Btu/h-ft-°F |  |  | 0.35043 | 0.34568 |  | 0.34229 | 0.34387
19 | Latent Heat |  |  | Btu/lb
20 | Inlet Pressure |  |  | psigg | (inlet) |  | 29.0075 |  |  | 60
21 | Velocity |  |  | ft/s |  |  | 3.7686 |  |  | 9.2574
22 | Press Drop Allow/Calc |  |  | psig |  |  | 1.5 | 3.5146 |  | 10 | 4.7813
23 | Fouling Factor |  |  | ft²-h-°F/Btu |  |  | 0.00049969 |  |  | 0.00049969
24 | Heat Exchanged |  |  | Btu/hr |  |  | 5002748.416 |  | LMTD (corrected) °F |  | 12.7413
25 | Service Coeff. |  |  | Btu/h-ft²-°F |  | Dirty |  | 319.3616 | Clean |  | 502.5535
26 | Construction Data for One Shell
27 |  |  |  |  | Shell Side |  | Tube Side |  | Sketch
28 | Design/Test Press |  |  | psigg
29 | Design Temperature |  |  | °F
30 | No. Passes per Shell |  |  |  | 1 |  | 1
31 | Corrosion Allowance |  |  | in
32 | Connections Size & Rating |  | In | inches | 12 |  | 16
33 |  |  | Out |  | 12 |  | 16
34 |  |  | Intermediate
35 | Tubes | No. | 308 | OD, in | 0.75 | Gauge | 14 | Length, ft. | 15 | Pitch layout, deg. |  | 90
36 |  | Type |  |  |  |  | Material | Cr-alloy (0.5% Cr) |  | Pitch ratio |  | 1.33
37 | Shell |  |  | OD, in |  | ID, in | 21.25 | Material
38 | Channel or Bonnet |  |  | OD, in |  | Thick |  | Channel Cover
39 | Tubesheet Type
40 | Floating Heat Cover | [6 empty] | Impingement Protection
41 | Baffles Cross (number) |  |  | 16 |  | % Cut (d) |  | 25% |  | Spacing C/C, in |  | 10
42 | Baffles Long |  |  |  |  | Seal Type No
43 | Supports Tube |  |  |  |  | U-Bend |  |  |  | Type
44 | Bypass Seal Arrangement |  |  |  | NA |  |  | Tube-Tubesheet Joint
45 | Expansion Joint No. | [6 empty] | Type
46 | Rho-V2-Inlet Nozzle |  |  | 986.8449 |  | Bundle Entrance |  | 278.7986 |  | Bundle Exit | 277.9001
47 | Gaskets - Shell Side | [6 empty] | Tube Side
48 | Floating Heat Cover | [6 empty] | Supports
49 | Code Requirements | [6 empty] | TEMA Class
50 | Weight per shell |  | lb | 7000 |  | Filled w/water |  | 9200 |  | Bundle | 4200
51
52 | Notes
53
54

## Conversions
Units conversion table. Do not change the SI units;
You may change the SI Units (and corresponding "Multiply to =")
but be very careful!
DO NOT INSERT ROWS INTO THIS TABLE!
Table Name: UNITS_CONV
Units Conversion
Index | Customary US |  | Multiply to = | SI Unit
1 | volume | gallons | 3.7854 | liters
2 | length | in | 25.4 | mm |  | The format for accessing the Units Conversion table is:
3 | area | ft² | 0.092903 | m² |  |  | =INDEX( units_conv, index, 2)
4 | heat flux | Btu/h-ft²-°F | 5.6783 | W/m²-°C |  |  | returns the second column (i.e., US units name)
5 | conductivity | Btu/h-ft-°F | 1.7307 | W/m-°C
6 | Heat transfer | Btu/hr | 0.2931 | W |  |  | Example
7 | flowrate | gal/min | 3.7854 | liters/min |  |  | Index = 8 (fouling)
8 | fouling | ft²-h-°F/Btu | 0.17611 | m²-°C/W |  |  | formula:
9 | pipe sizes | inches |  | DN |  |  | result:
10 | spec heat | Btu/lb-°F | 4.1868 | kJ/kg-°C
11 | length | feet | 304.8 | millimeters
12 | velocity | ft/s | 0.3048 | m/s |  | 3.2808
13 | area | ft² | 0.092903 | m²
14 | pressure | psig | 6.8948 | kPa(g)
15 | mass flow | lb/h | 0.45359 | kg/h
16 | heat of vap | Btu/lb | 2.326 | kJ/kg
17 | dynamic viscosity | lb/ft-h | 0.00041338 | kg/m-s
18 | density | lb/ft3 | 16.0185 | kg/m3
Units | 1 | 2 |  | User Inputs | FALSE
Solve For | 6 |  |  | Calc Results | FALSE
Distilled Water | Shell | 2 |  | Mech Detail | FALSE
Raw Water | Tubes |  |  | General Inputs | FALSE
| Tube Diameters |  |  |  |  | Tube Gauges
| in | US | SI | US |  | Min | Max
| 0.25 | 0.25 | 6.35 | 0.25 |  | 18 | 27
| 0.375 | 0.375 | 9.53 | 0.375 |  | 14 | 24
| 0.5 | 0.5 | 12.7 | 0.5 |  | 13 | 24
| 0.625 | 0.625 | 15.88 | 0.625 |  | 12 | 24
| 0.75 | 0.75 | 19.05 | 0.75 |  | 10 | 24
| 1 | 1 | 25.4 | 1 |  | 8 | 24
| 1.25 | 1.25 | 31.75 | 1.25 |  | 8 | 24
| 1.5 | 1.5 | 38.1 | 1.5 |  | 8 | 24
| 2 | 2 | 50.8 | 2 |  | 4 | 24
| Units Conversion |  | to SI | 19.05 |  | 10
|  |  | to US | #N/A |  | 24
Wall Thickness
| Gauge | BWG | ISG | Brown&Sharp
| 4 | 0.238 | 0.232 | 0.204
| 5 | 0.22 | 0.212 | 0.182
| 6 | 0.203 | 0.192 | 0.162
| 7 | 0.18 | 0.176 | 0.144
| 8 | 0.165 | 0.16 | 0.128
| 9 | 0.148 | 0.144 | 0.114
| 10 | 0.134 | 0.128 | 0.102
| 11 | 0.12 | 0.116 | 0.091
| 12 | 0.109 | 0.104 | 0.081
| 13 | 0.095 | 0.092 | 0.072
| 14 | 0.083 | 0.08 | 0.064
| 15 | 0.072 | 0.072 | 0.057
| 16 | 0.065 | 0.064 | 0.051
| 17 | 0.058 | 0.056 | 0.045
| 18 | 0.049 | 0.048 | 0.04
| 19 | 0.042 | 0.04 | 0.036
| 20 | 0.035 | 0.036 | 0.032
| 21 | 0.032 | 0.032 | 0.029
| 22 | 0.028 | 0.028 | 0.025
| 23 | 0.025 | 0.024 | 0.023
| 24 | 0.022 | 0.022 | 0.02
| 25 | 0.02 | 0.02 | 0.018
| 26 | 0.018 | 0.018 | 0.016
| 27 | 0.016 | 0.016 | 0.014
Tube Parameters based on Pitch
| Arrangement | Parallel | Normal
| 30 | 0.86603 | 1
| 45 | 0.70711 | 1.4142
| 60 | 0.5 | 1.7321
| 90 | 1 | 1
| Standard Shell Sizes, Inside Diameter | [5 empty] | Shell Thickness |  |  | Flange Weight
|  |  | inches | inches | mm | mm | inches | OD, inches | OD, mm | lb | lb | kg
| 7.981 | 10.02 | 7.981 | 10.02 | 203 | 255 | 0.644 | 8.625 | 219.075 | 28 | 28 | 13
| 10.02 | 12 | 10.02 | 12 | 255 | 305 | 0.73 | 10.75 | 273.05 | 40 | 40 | 18
| 12 | 13.25 | 12 | 13.25 | 305 | 337 | 0.75 | 12.75 | 323.85 | 61 | 61 | 28
| 13.25 | 15.25 | 13.25 | 15.25 | 337 | 387 | 0.75 | 14 | 355.6 | 83 | 83 | 38
| 15.25 | 17.25 | 15.25 | 17.25 | 387 | 438 | 0.75 | 16 | 406.4 | 106 | 106 | 48
| 17.25 | 19.25 | 17.25 | 19.25 | 438 | 489 | 0.75 | 18 | 457.2 | 108 | 108 | 49
| 19.25 | 21.25 | 19.25 | 21.25 | 489 | 540 | 0.75 | 20 | 508 | 148 | 148 | 67
| 21.25 | 23.25 | 21.25 | 23.25 | 540 | 591 | 0.75 | 22 | 558.8 | 180 | 204 | 93
| 23.25 | 25 | 23.25 | 25 | 591 | 635 | 0.75 | 24 | 609.6 | 204 | 204 | 93
| 25 | 27 | 25 | 27 | 635 | 686 | 1 | 26 | 660.4 | 210 | 210 | 95
| 27 | 29 | 27 | 29 | 686 | 737 | 1 | 28 | 711.2 | 230 | 230 | 105
| 29 | 31 | 29 | 31 | 737 | 787 | 1 | 30 | 762 | 240 | 240 | 109
| 31 | 33 | 31 | 33 | 787 | 838 | 1 | 32 | 812.8 | 260 | 260 | 118
| 33 | 35 | 33 | 35 | 838 | 889 | 1 | 34 | 863.6 | 270 | 270 | 123
| 35 | 37 | 35 | 37 | 889 | 940 | 1 | 36 | 914.4 | 185 | 185 | 84
| 37 | 39 | 37 | 39 | 940 | 991 | 1 | 38 | 965.2 | 300 | 300 | 136
| 39 | 42 | 39 | 42 | 991 | 1067 | 1 | 40 | 1016 | 310 | 310 | 141
| 42 | 45 | 42 | 45 | 1067 | 1143 | 1 | 43 | 1092.2 | 330 | 330 | 150
| 45 | 48 | 45 | 48 | 1143 | 1219 | 1 | 46 | 1168.4 | 360 | 360 | 164
| 48 | 54 | 48 | 54 | 1219 | 1372 | 1 | 49 | 1244.6 | 380 | 380 | 173
| 54 | 60 | 54 | 60 | 1372 | 1524 | 1 | 55 | 1397 | 420 | 420 | 191
| 60 | 66 | 60 | 66 | 1524 | 1676 | 1 | 61 | 1549.4 | 460 | 460 | 209
| 66 | 72 | 66 | 72 | 1676 | 1829 | 1 | 67 | 1701.8 | 505 | 505 | 230
| 72 | 78 | 72 | 78 | 1829 | 1981 | 1 | 73 | 1854.2 | 550 | 550 | 250
| 78 | 84 | 78 | 84 | 1981 | 2134 | 1 | 79 | 2006.6 | 590 | 590 | 268
| 84 | 90 | 84 | 90 | 2134 | 2286 | 1 | 85 | 2159 | 630 | 630 | 286
| 90 | 96 | 90 | 96 | 2286 | 2438 | 1 | 91 | 2311.4 | 675 | 675 | 307
| 96 | 108 | 96 | 108 | 2438 | 2743 | 1 | 97 | 2463.8 | 720 | 720 | 327
| 108 | 120 | 108 | 120 | 2743 | 3048 | 1 | 109 | 2768.6 | 805 | 805 | 366
| 120 | 132 | 120 | 132 | 3048 | 3353 | 1 | 121 | 3073.4 | 890 | 890 | 405
Correlation Coefficients for j-I and f-I
| Pitch Layout | Nre | a1 | a2 | a3 | a4 | b1 | b2 | b3 | b4
| 30 | 0 | 1.4 | -0.667 | 1.45 | 0.519 | 48 | -1 | 7 | 0.5
| 30 | 10 | 1.36 | -0.657 | 1.45 | 0.519 | 45.1 | -0.973 | 7 | 0.5
| 30 | 100 | 0.593 | -0.477 | 1.45 | 0.519 | 4.57 | -0.476 | 7 | 0.5
| 30 | 1000 | 0.321 | -0.388 | 1.45 | 0.519 | 0.486 | -0.152 | 7 | 0.5
| 30 | 10000 | 0.321 | -0.388 | 1.45 | 0.519 | 0.372 | -0.123 | 7 | 0.5
| 45 | 0 | 1.55 | -0.667 | 1.93 | 0.5 | 32 | -1 | 6.59 | 0.52
| 45 | 10 | 0.498 | -0.656 | 1.93 | 0.5 | 26.2 | -0.913 | 6.59 | 0.52
| 45 | 100 | 0.73 | -0.5 | 1.93 | 0.5 | 3.5 | -0.476 | 6.59 | 0.52
| 45 | 1000 | 0.37 | -0.396 | 1.93 | 0.5 | 0.333 | -0.136 | 6.59 | 0.52
| 45 | 10000 | 0.37 | -0.396 | 1.93 | 0.5 | 0.303 | -0.126 | 6.59 | 0.52
| 60 | 0 | 1.4 | -0.667 | 1.45 | 0.519 | 48 | -1 | 7 | 0.5
| 60 | 10 | 1.36 | -0.657 | 1.45 | 0.519 | 45.1 | -0.973 | 7 | 0.5
| 60 | 100 | 0.593 | -0.477 | 1.45 | 0.519 | 4.57 | -0.476 | 7 | 0.5
| 60 | 1000 | 0.321 | -0.388 | 1.45 | 0.519 | 0.486 | -0.152 | 7 | 0.5
| 60 | 10000 | 0.321 | -0.388 | 1.45 | 0.519 | 0.372 | -0.123 | 7 | 0.5
| 90 | 0 | 0.97 | 0.667 | 1.187 | 0.37 | 35 | -1 | 6.3 | 0.378
| 90 | 10 | 0.9 | -0.631 | 1.187 | 0.37 | 32.1 | -0.0963 | 6.3 | 0.378
| 90 | 100 | 0.408 | -0.46 | 1.187 | 0.37 | 6.09 | -0.602 | 6.3 | 0.378
| 90 | 1000 | 0.107 | -0.266 | 1.187 | 0.37 | 0.0815 | -0.022 | 6.3 | 0.378
| 90 | 10000 | 0.37 | -0.395 | 1.187 | 0.37 | 0.391 | -0.148 | 6.3 | 0.378
Tube Materials and Thermal Conductivities | bar: a1 to a2
| Aluminum | 130 | a1: 130
| Brass (75% Cu, 30% Zn) | 72 | a1: 72
| Bronze (75% Cu, 25% Sn) | 15 | a1: 15
| Cr-alloy (0.5% Cr) | 24 | a1: 24.4
| Constantan (60% Cu, 40% Ni) | 14 | a1: 14
| Copper | 220 | a1: 220
| Iron | 26 | a1: 26
| Magnesium | 95 | a1: 95
| Molybdenum | 64 | a1: 64
| Nickel | 43 | a1: 43
| Steel (1% C) | 20 | a1: 20
| Steel (1% Cr) | 27 | a1: 27
| Steel (18% Cr, 8% Ni) | 12 | a1: 12
| Zinc | 58 | a1: 58
Pipe Sizes
|  | ID | Pipe Size | Nozzle Wt | ID | Pipe Size | Nozzle Wt | ID | Pipe Size | Nozzle Wt
|  | in | in | lb | in | in | lb | mm | DN | kg
|  | 1.049 | 1 | 3 | 1.049 | 1 | 3 | 26.6446 | 25 | 1.3636
| 1.049 | 1.61 | 1.5 | 4 | 1.61 | 1.5 | 4 | 40.894 | 40 | 1.8182
| 1.61 | 2.067 | 2 | 6 | 2.067 | 2 | 6 | 52.5018 | 50 | 2.7273
| 2.067 | 3.26 | 3 | 12 | 3.26 | 3 | 12 | 82.804 | 80 | 5.4545
| 3.26 | 4.26 | 4 | 17 | 4.26 | 4 | 17 | 108.204 | 100 | 7.7273
| 4.26 | 6.357 | 6 | 28 | 6.357 | 6 | 28 | 161.4678 | 150 | 12.7273
| 6.357 | 8.329 | 8 | 44 | 8.329 | 8 | 44 | 211.5566 | 200 | 20
| 8.329 | 10.42 | 10 | 56 | 10.42 | 10 | 56 | 264.668 | 250 | 25.4545
| 10.42 | 12.39 | 12 | 90 | 12.39 | 12 | 90 | 314.706 | 300 | 40.9091
| 12.39 | 13.624 | 14 | 118 | 13.624 | 14 | 118 | 346.0496 | 350 | 53.6364
| 13.624 | 15.624 | 16 | 146 | 15.624 | 16 | 146 | 396.8496 | 400 | 66.3636
| 15.624 | 17.624 | 18 | 170 | 17.624 | 18 | 170 | 447.6496 | 450 | 77.2727
| 17.624 | 19.564 | 20 | 202 | 19.564 | 20 | 202 | 496.9256 | 500 | 91.8182
| 19.564 | 23.5 | 24 | 275 | 23.5 | 24 | 275 | 596.9 | 600 | 125
This worksheet has intermediate values and radio button links; do not change or delete

## Fluid Data
Use this area to enter raw data. The coefficients are calculated, ready to be pasted (use "Paste Special… Values") onto the corresponding line in the HTF_properties table
To remove an entry from the database, use Tools… Protection… Unprotect, then delete the row with the offending compound |  |  | Units that the original data are in: | [22 empty] | Selection Values for Radio Buttons - this worksheet | [31 empty] | Fluid Name: |  | Acetic Acid |  | <-- Already in the database |  |  | Fluid Name: |  | Propyl Alcohol, i- |  | <-- Already in the database
|  |  | Temperature | [22 empty] | Temperature |  |  | 2 | [28 empty] | Manufacturer: | [6 empty] | Manufacturer:
|  |  | Density | [8 empty] | 5.16 | 38.5995 | [12 empty] | Specific Gravity |  |  | 2 | [28 empty] | Description: |  | pure component |  |  | Heat Vap | 395 | Description: |  | pure component |  |  | Heat Vap | 663
|  |  | Specific Heat | [22 empty] | Specific Heat |  |  | 2 | [28 empty] | Operating range: |  |  | °C minimum |  | FP | 39 | Operating range: |  |  | °C minimum |  | FP | 12
|  |  | Thermal Conductivity | [22 empty] | Thermal Conductivity |  |  | 2 | [31 empty] | °C maximum |  | BP | 118.1 |  |  |  | °C maximum |  | BP | 82.5
|  |  | Viscosity | [22 empty] | Viscosity |  |  | 1 | [28 empty] | Source: |  | Perry's, 6th Ed |  |  | Mol Wt | 60.05 | Source: |  | Perry's, 6th Ed |  |  | Mol Wt | 60.1
|  |  | Heat of Vaporization | [22 empty] | Heat of Vaporization |  |  | 2
[29 empty] | 0 | [29 empty] | Liquid |  | Thermal |  | Vapor |  |  | Liquid |  | Thermal |  | Vapor
|  |  | Fluid Name: |  | Octane |  | <-- Already in the database | [50 empty] | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure |  | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure
|  |  | Manufacturer: | [54 empty] | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg |  | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg
|  |  | Description: |  | pure component |  |  | Heat Vap | 302.38 | [48 empty] | 0 | 1068.6667 | 0.468 | 0.099 | 1.8 |  |  | -10 | 809.7536 | 0.55 | 0.094 | 4.8
|  |  | Operating range: |  |  | °C minimum |  | FP | 13.3333 | [48 empty] | 20 | 1048.6667 | 0.485 | 0.099 | 2.28 | 11.68 |  | 0 | 801.5741 | 0.58 | 0.093 | 3.7 | 8.42
[6 empty] | °C maximum |  | BP | 125.6667 | [48 empty] | 40 | 1028.6667 | 0.503 | 0.099 | 0.95 |  |  | 20 | 785.2152 | 0.641 | 0.092 | 2.25
|  |  | Source: |  | Yaw's Handbook, 2003 |  |  | Mol Wt | 114.231 | [48 empty] | 60 | 1008.6667 | 0.52 | 0.099 | 0.75 | 89.74 |  | 40 | 768.8563 | 0.702 | 0.091 | 1.35 | 107.2
[10 empty] | Values converted to SI units for the htf_properties table | [16 empty] | Predicted values in units of the table |  |  |  |  | Predicted values in same units as input | [25 empty] | 80 | 988.6667 | 0.54 | 0.099 | 0.6 |  |  | 60 | 752.4973 | 0.76 | 0.09 | 0.87
|  |  |  | Liquid |  | Thermal |  | Vapor | Vapor |  |  |  |  | Thermal |  | Intermediate | [10 empty] | Liquid |  | Thermal |  |  | Liquid |  | Thermal | [23 empty] | 100 | 968.6667 | 0.56 | 0.099 | 0.48 | 424.1 |  | 80 | 736.1384 | 0.825 | 0.089 | 0.56 | 690.48
|  |  | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure |  | Temperature |  | Density | Sp. Heat | Conduct. | Visc. | Calcs | [9 empty] | Temp. | Density | Sp. Heat | Conduct. | Visc. |  | Density | Sp. Heat | Conduct. | Visc.
|  |  | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg |  | deg C | deg K | kg/m3 | kJ/kg-K | W/m-K | mPa-s | 0.66639 | [9 empty] | °C | kg/m3 | kJ/kg-K | W/m-K | mPa-s |  | kg/cu.m. | kJ/kg-K | W/m-K | cP | [22 empty] | Fluid Name: |  | Methyl Alcohol |  | <-- Already in the database |  |  | Fluid Name: |  | Glycerol |  | <-- Already in the database
|  | Enter values at SIX temperatures -->>> | -20 | 732.5191 | 2.1285 | 0.14198 | 1.0076 | 0.67936 |  | -20 | 253.15 | 732.5191 | 2.1285 | 0.14198 | 1.0076 | [10 empty] | -20 | 734.9717 | 2.1088 | 0.14262 | 0.89633 |  | 734.9717 | 2.1088 | 0.14262 | 0.89633 | [22 empty] | Manufacturer: | [6 empty] | Manufacturer:
|  |  | 20 | 702.5186 | 2.2182 | 0.13053 | 0.55915 | 10.5791 |  | 20 | 293.15 | 702.5186 | 2.2182 | 0.13053 | 0.55915 | [10 empty] | 20 | 701.4944 | 2.2234 | 0.13021 | 0.55915 |  | 701.4944 | 2.2234 | 0.13021 | 0.55915 | [22 empty] | Description: |  |  |  |  | Heat Vap | 1100 | Description: |  | pure component |  |  | Heat Vap | 663
|  |  | 60 | 670.5874 | 2.3152 | 0.11845 | 0.36575 | 77.8082 |  | 60 | 333.15 | 670.5874 | 2.3152 | 0.11845 | 0.36575 | [10 empty] | 60 | 668.0171 | 2.3379 | 0.1178 | 0.37107 |  | 668.0171 | 2.3379 | 0.1178 | 0.37107 | [22 empty] | Operating range: |  |  | °C minimum |  | FP | 12 | Operating range: |  |  | °C minimum |  | FP | 160
|  |  | 100 | 636.161 | 2.4352 | 0.10573 | 0.25901 | 349.6937 |  | 100 | 373.15 | 636.161 | 2.4352 | 0.10573 | 0.25901 | 0.82609 | [9 empty] | 100 | 634.5398 | 2.4525 | 0.10539 | 0.25901 |  | 634.5398 | 2.4525 | 0.10539 | 0.25901 | [25 empty] | °C maximum |  | BP | 64.7 |  |  |  | °C maximum |  | BP | 290
|  |  | 120 | 617.7531 | 2.5086 | 0.099123 | 0.22073 | 648.6166 |  | 120 | 393.15 | 617.7531 | 2.5086 | 0.099123 | 0.22073 | [10 empty] | 120 | 617.8012 | 2.5098 | 0.099179 | 0.2199 |  | 617.8012 | 2.5098 | 0.099179 | 0.2199 | [22 empty] | Source: |  |  |  |  | Mol Wt | 32.04 | Source: |  | Perry's, 6th Ed |  |  | Mol Wt | 92.1
|  |  | 140 | 598.3474 | 2.5937 | 0.092362 | 0.18848 | 1121.7379 |  | 140 | 413.15 | 598.3474 | 2.5937 | 0.092362 | 0.18848 | [10 empty] | 140 | 601.0625 | 2.567 | 0.092973 | 0.18848 |  | 601.0625 | 2.567 | 0.092973 | 0.18848
[59 empty] | Liquid |  | Thermal |  | Vapor |  |  | Liquid |  | Thermal |  | Vapor
[58 empty] | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure |  | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure
[58 empty] | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg |  | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg
[58 empty] | -10 | 819.4333 | 0.565 | 0.124 | 0.92 |  |  | 60 | 1136.555 | 0.62 | 0.164 | 92
[58 empty] | 0 | 810.1833 | 0.578 | 0.124 | 0.8 | 29.6 |  | 80 | 1084.291 | 0.645 | 0.164 | 34
[58 empty] | 10 | 800.9333 | 0.588 | 0.124 | 0.69 |  |  | 100 | 1032.027 | 0.67 | 0.164 | 13.5
|  | The charts graph the input and predicted data. Large deviations may indicate a data entry error | [55 empty] | 20 | 791.6833 | 0.594 | 0.124 | 0.6 | 96.7 |  | 120 | 979.763 | 0.694 | 0.164 | 5.4
[58 empty] | 30 | 782.4333 | 0.608 | 0.124 | 0.52 |  |  | 140 | 927.499 | 0.72 | 0.164 | 2.4
[58 empty] | 40 | 773.1833 | 0.618 | 0.124 | 0.47 | 265.6 |  | 160 | 875.235 | 0.743 | 0.164 | 1
[58 empty] | Fluid Name: |  | Ethyl Alcohol |  | <-- Already in the database |  |  | Fluid Name: |  | Butyl Alcohol, n- |  | <-- Already in the database
[58 empty] | Manufacturer: | [6 empty] | Manufacturer:
[58 empty] | Description: |  | pure component |  |  | Heat Vap | 842 | Description: |  | pure component |  |  | Heat Vap | 581
[58 empty] | Operating range: |  |  | °C minimum |  | FP | 13 | Operating range: |  |  | °C minimum |  | FP | 29
[61 empty] | °C maximum |  | BP | 78.4 |  |  |  | °C maximum |  | BP | 117.5
[58 empty] | Source: |  | Perry's, 6th Ed |  |  | Mol Wt | 46.07 | Source: |  | Perry's, 6th Ed |  |  | Mol Wt | 74.12
[59 empty] | Liquid |  | Thermal |  | Vapor |  |  | Liquid |  | Thermal |  | Vapor
[58 empty] | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure |  | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure
[58 empty] | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg |  | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg
[58 empty] | -10 | 815.04 | 0.457 | 0.105 | 2.07 |  |  | 0 |  | 0.5 | 0.101 | 4.7
[58 empty] | 0 | 806.45 | 0.49 | 0.105 | 1.7 | 11.97 |  | 20 |  | 0.555 | 0.099 | 2.9 | 4.86
[58 empty] | 10 | 797.86 | 0.525 | 0.105 | 1.4 |  |  | 40 |  | 0.61 | 0.097 | 1.8
[58 empty] | 20 | 789.27 | 0.562 | 0.105 | 1.19 | 44.25 |  | 60 |  | 0.67 | 0.095 | 1.18 | 60.39
[58 empty] | 30 | 780.68 | 0.598 | 0.105 | 0.98 |  |  | 80 |  | 0.72 | 0.093 | 0.79
[6 empty] | Antoine Coefficients |  |  | Viscosity Constants |  |  | Density = mt(deg C) + b |  | thermal conductivity |  | heat capacity | [41 empty] | 40 | 772.09 | 0.636 | 0.105 | 0.85 | 135 |  | 100 |  | 0.78 | 0.091 | 0.55 | 386.72
[6 empty] | A | B | C | A | B | C | m | b | m | b | m | b
Octane | 0 | pure component | 0 | 0 |  | 7.0958 | 1455.3137 | 219.7033 | -6.8339 | 3563.9671 | 276.8476 | -0.83693 | 718.2331 | -0.00031032 | 0.13642 | 0.0028639 | 2.1661 | 13.3333 | 125.6667 |  | 114.231 | 302.38 | -20 | 20 | 60 | 100 | 120 | 140 | 732.5191 | 702.5186 | 670.5874 | 636.161 | 617.7531 | 598.3474 | 2.1285 | 2.2182 | 2.3152 | 2.4352 | 2.5086 | 2.5937 | 0.14198 | 0.13053 | 0.11845 | 0.10573 | 0.099123 | 0.092362 | 1.0076 | 0.55915 | 0.36575 | 0.25901 | 0.22073 | 0.18848 | 10.5791 | 349.6937 | 1121.7379 | Yaw's Handbook, 2003 | 114.231 | Fluid Name: |  | Propyl Alcohol, n- |  | <-- Already in the database
Manufacturer:
[23 empty] | Raw Data - Units may be converted from original source | [34 empty] | Description: |  | pure component |  |  | Heat Vap | 695
Fluid Name | Manufacturer | Description | Temp Use Range (deg C) |  |  | Antoine Coefficients A: LOG(VP, mm Hg) = A + B / ((t, deg C) + C); Viscosity Constants A: cP = EXP(A+B/((T, deg K)+C)); Density = mt(deg C) + b m: kg/m3 = mt(deg C) + b; thermal conductivity m: W/m-K = mt(deg C) + b; heat capacity m: kJ/kg-K = mt(deg C) + b | Flash Point | Boiling Point | Type | Molecular Wt | Heat Vap | Temperature Points, deg C | [5 empty] | Density, kg/m3 | [5 empty] | Specific Heat, kJ/kg-K | [5 empty] | Thermal Conductivity, W/m-K | [5 empty] | Viscosity, Pa-s | [5 empty] | Vapor Pressure, mmHg |  |  | Source | MW | Operating range: |  |  | °C minimum |  | FP | 15
|  |  | Liquid | [5 empty] | A | B | C | m | b | m | b | m | b |  |  |  |  | kJ/kg | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | 4 | 5 | 6 | 1 | 2 | 3 | [5 empty] | °C maximum |  | BP | 97.8
|  |  | Low | High | [53 empty] | Source: |  | Perry's, 6th Ed |  |  | Mol Wt | 60.1
Acetic Acid | 0 | pure component | 0 | 0 |  | 7.6128 | 1673.3465 | 235.6539 | -1.7788 | 139.6282 | -239.5073 | -1 | 1068.6667 | 0 | 0.17134 | 0.0038399 | 1.9544 | 39 | 118.1 |  | 60.05 | 395 | 0 | 20 | 40 | 60 | 80 | 100 | 1068.6667 | 1048.6667 | 1028.6667 | 1008.6667 | 988.6667 | 968.6667 | 1.9594 | 2.0306 | 2.106 | 2.1771 | 2.2609 | 2.3446 | 0.17134 | 0.17134 | 0.17134 | 0.17134 | 0.17134 | 0.17134 | 1.8 | 2.28 | 0.95 | 0.75 | 0.6 | 0.48 | 11.68 | 89.74 | 424.1 | Perry's, 6th Ed
Butane, n | 0 | pure component | 0 | 0 |  | 6.8325 | 946.4096 | 240.0761 | -5.369 | 1681.6871 | 167.1522 | -1.0319 | 601.637 | -0.00050178 | 0.11679 | 0.0035019 | 2.3031 | -59.4444 | -0.44444 |  | 58.123 | 386.116 | -60 | -40 | -30 | -20 | -10 | 10 | 662.6555 | 643.1988 | 633.155 | 622.8756 | 612.3381 | 590.3786 | 2.1024 | 2.1603 | 2.1921 | 2.2263 | 2.2635 | 2.3485 | 0.14671 | 0.13693 | 0.13196 | 0.12694 | 0.12187 | 0.11159 | 0.3962 | 0.31102 | 0.28038 | 0.25466 | 0.23247 | 0.19507 | 126.5486 | 340.5112 | 1116.9127 | Yaw's Handbook, 2003
Butyl Alcohol, n- | 0 | pure component | 0 | 0 |  | 7.9116 | 1619.0414 | 204.0888 | -9.9402 | 4947.1689 | 156.3931 | -0.8 | 810 | -0.00017307 | 0.1748 | 0.011693 | 2.0914 | 29 | 117.5 |  | 74.12 | 581 | 0 | 20 | 40 | 60 | 80 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0934 | 2.3237 | 2.5539 | 2.8052 | 3.0145 | 3.2657 | 0.1748 | 0.17134 | 0.16788 | 0.16442 | 0.16096 | 0.1575 | 4.7 | 2.9 | 1.8 | 1.18 | 0.79 | 0.55 | 4.86 | 60.39 | 386.72 | Perry's, 6th Ed
CALFLO™ AF | Petro-Canada | 99.9% pure base oils, crystal-clear, free of aromatic compounds with additives | 15 | 315 |  | 2.2623 | 59.8606 | -25.9558 | -2.8101 | 862.7299 | -172.1586 | -0.61887 | 876.7097 | -5.3969e-05 | 0.14366 | 0.0032985 | 1.837 | 225 | 365 | Paraffinic |  |  | 15 | 40 | 40 | 100 | 260 | 316 | 866.5987 | 852.1821 | 852.1821 | 815.3396 | 716.0252 | 680.7846 | 1.8841 | 1.9678 | 1.9678 | 2.1771 | 2.6796 | 2.8889 | 0.14192 | 0.14192 | 0.14192 | 0.13846 | 0.12981 | 0.12634 | 0 | 27.355 | 0 | 4.4028 | 0 | 0.47655 | 0.01 | 28.4354 | 113.7415 | Petro-Canada, TechData Sheet IM-7852E (06.08)
CALFLO™ HTF | Petro-Canada | 99.9% pure base oils, crystal-clear, free of aromatic compounds with additives | 15 | 326 |  | 2.1457 | 63.3161 | -24.7274 | -3.0195 | 971.167 | -162.4419 | -0.63705 | 880.3808 | -5.2404e-05 | 0.14404 | 0.0032985 | 1.837 | 231 | 370 | Paraffinic |  |  | 15 | 40 | 40 | 100 | 260 | 316 | 869.8024 | 855.3858 | 855.3858 | 816.9415 | 714.4233 | 679.1827 | 1.8841 | 1.9678 | 1.9678 | 2.1771 | 2.6796 | 2.8889 | 0.14365 | 0.14192 | 0.14192 | 0.13846 | 0.12981 | 0.12807 | 0 | 30.7083 | 0 | 4.9016 | 0 | 0.47543 | 0.01 | 20.1633 | 84.7891 | Petro-Canada, TechData Sheet IM-7851E (07.06)
CALFLO™ LT | Petro-Canada | Synthetic poly-alpha-olefins | 4 | 288 |  | -3.077 | 295.8074 | -314.6611 | -2.9443 | 771.2802 | -150.4749 | -0.65897 | 829.7925 | -8.5826e-05 | 0.14349 | 0.0036072 | 1.9915 | 176 | 318 |  |  |  | 15 | 40 | 40 | 100 | 260 | 260 | 818.5433 | 804.1267 | 804.1267 | 764.0805 | 658.3587 | 658.3587 | 2.0515 | 2.1353 | 2.1353 | 2.3446 | 2.9308 | 2.9308 | 0.14192 | 0.14019 | 0.14019 | 0.135 | 0.12115 | 0.12115 | 0 | 6.031 | 0 | 1.681 | 0 | 0.39502 | 0.01 | 0.02 | 216.1088 | Petro-Canada, TechData Sheet IM-7874E (07.07)
Chemtherm® 550 | Coastal Chemical | Premium oil more thermally stable than mineral oils | 93.3333 | 315.5556 |  | -37.9838 | 123237.0069 | -3346.097 | -2.72 | 756.1805 | -187.0606 | -0.63433 | 909.7845 | -7.5302e-05 | 0.13261 | 0.0034882 | 1.854 | 172.7778 | 273.3333 |  |  |  | 37.7778 | 93.3333 | 148.8889 | 204.4444 | 260 | 315.5556 | 885.8208 | 850.5802 | 815.3396 | 780.099 | 744.8584 | 709.6178 | 2.0097 | 2.1771 | 2.3446 | 2.5539 | 2.7633 | 2.9726 | 0.12981 | 0.12548 | 0.1215 | 0.11717 | 0.11302 | 0.10886 | 30.2065 | 4.457 | 1.6551 | 0.88931 | 0.58844 | 0.43287 | 0.8 | 17.5 | 480 | Chemtherm 550 Data Sheet, 2010
Chemtherm® 650 | Coastal Chemical | Premium high temperature oil resists oxidation | 10 | 343.3333 |  | 9.4851 | 4973.2232 | 486.5437 | -3.8872 | 1148.4154 | -77.4589 | -0.7968 | 998.9694 | -0.00013076 | 0.12836 | 0.0037385 | 1.3118 | 135 | 270 |  |  |  | 10 | 37.7778 | 121.1111 | 204.4444 | 260 | 343.3333 | 986.7371 | 967.515 | 906.6448 | 840.9692 | 794.5156 | 719.2289 | 1.3188 | 1.4528 | 1.7794 | 2.1143 | 2.3027 | 2.5539 | 0.12756 | 0.12323 | 0.1125 | 0.1009 | 0.094325 | 0.083941 | 4.7363 | 2.8058 | 0.75252 | 0.36162 | 0.25424 | 0.17261 | 1 | 194 | 3107 | Chemtherm 650 Data Sheet, 2010
Chemtherm® 700 | Coastal Chemical | Premium high temperature single compound formulation | 37.7778 | 351.6667 |  | 28.9798 | 69967.7155 | 2296.208 | -2.8524 | 801.5979 | -167.467 | -0.69941 | 1043.8233 | -0.00010361 | 0.13288 | 0.0035334 | 1.4824 | 212.7778 | 360 |  |  |  | 37.7778 | 93.3333 | 148.8889 | 204.4444 | 260 | 315.5556 | 1017.1722 | 978.7279 | 940.2836 | 900.2375 | 861.7931 | 823.3488 | 1.6119 | 1.8213 | 2.0055 | 2.1981 | 2.4074 | 2.5958 | 0.12894 | 0.12323 | 0.11734 | 0.11163 | 0.10644 | 0.099863 | 14.2404 | 3.2396 | 1.4104 | 0.7652 | 0.51708 | 0.38697 | 0.5 | 10 | 155 | Chemtherm 700 Data Sheet, 2010
Diphyl® | LANXESS Deutschland GmbH | High-temperature HTF based on diphenyl oxide/diphenyl eutectic for liq and vap phase | 13 | 400 |  | 7.2022 | 1946.5679 | 193.6808 | -2.9562 | 695.5106 | -136.2796 | -1.0246 | 1094.601 | -0.00016387 | 0.1465 | 0.0026839 | 1.5037 | 115 | 257 |  |  |  | 20 | 60 | 100 | 200 | 300 | 400 | 1061 | 1031 | 998 | 905 | 796 | 670 | 1.557 | 1.665 | 1.772 | 2.041 | 2.309 | 2.577 | 0.144 | 0.137 | 0.13 | 0.112 | 0.097 | 0.082 | 4.26 | 1.78 | 0.99 | 0.41 | 0.26 | 0.19 | 0.338 | 181 | 8383 | DIPHYL® database Version 2.3 - August 2005
Diphyl® DT | LANXESS Deutschland GmbH | Isomeric ditolyl ethers with broad spectrum of applications in liq phase | -30 | 330 |  | -5.0998 | 4803.754 | -906.2417 | -2.6344 | 587.9923 | -159.4111 | -0.87116 | 1047.8925 | -0.00014486 | 0.1373 | 0.0027555 | 1.5304 | 135 | 284 |  |  |  | -30 | 10 | 90 | 170 | 250 | 330 | 1062 | 1037 | 980 | 913 | 835 | 746 | 1.448 | 1.558 | 1.778 | 1.999 | 2.219 | 2.44 | 0.142 | 0.136 | 0.124 | 0.112 | 0.101 | 0.09 | 71.21 | 8.31 | 1.31 | 0.57 | 0.36 | 0.27 | 1.82 | 26.6 | 1724 | DIPHYL® database Version 2.3 - August 2005
Diphyl® KT | LANXESS Deutschland GmbH | Synthetic mixture of isomeric bynzyl toluenes with high thermal stability | -45 | 350 |  | 8.8245 | 3748.7167 | 336.9459 | -3.2905 | 883.4734 | -119.0185 | -0.78788 | 1021.9644 | -0.00013226 | 0.13159 | 0.00295 | 1.53 | 146 | 290 |  |  |  | -40 | 0 | 80 | 160 | 240 | 320 | 1046 | 1021 | 965 | 904 | 836 | 761 | 1.412 | 1.53 | 1.766 | 2.002 | 2.238 | 2.474 | 0.136 | 0.131 | 0.122 | 0.112 | 0.1 | 0.088 | 84.76 | 11.49 | 1.63 | 0.62 | 0.35 | 0.24 | 0.005 | 19.1 | 1313 | DIPHYL® database Version 2.3 - August 2005
Diphyl® THT | LANXESS Deutschland GmbH | Partially hydrogenated terphenyls for pressureless high temperature applications | 0 | 345 |  | 35.7643 | 93078.0316 | 2471.7494 | -2.5681 | 631.4446 | -209.1473 | -0.76329 | 1038.6704 | -9.9322e-05 | 0.12406 | 0.0033797 | 1.5352 | 190 | 352 |  |  |  | 20 | 60 | 100 | 180 | 260 | 360 | 1018 | 992 | 965 | 907 | 844 | 758 | 1.603 | 1.738 | 1.873 | 2.143 | 2.414 | 2.752 | 0.12 | 0.118 | 0.115 | 0.108 | 0.1 | 0.086 | 135.78 | 12.48 | 3.62 | 1.02 | 0.53 | 0.34 | 0.1 | 4.61 | 785 | DIPHYL® database Version 2.3 - August 2005
DOWCAL™ 10/DOWTHERM™ 10 - 30 vol% | Dow Chemical | Ethylene glycol with inhibitor package | -10 | 170 |  |  |  |  | -4.1808 | 909.7339 | -107.5954 | -0.69488 | 1059.3277 | 0.00032369 | 0.45846 | 0.0027557 | 3.6177 | [5 empty] | 0 | 25 | 50 | 100 | 150 | 170 | 1051 | 1042 | 1031 | 999 | 955 | 934 | 3.62 | 3.69 | 3.75 | 3.89 | 4.03 | 4.09 | 0.437 | 0.467 | 0.491 | 0.514 | 0.507 | 0.495 | 3.82 | 1.81 | 1.03 | 0.47 | 0.28 | 0.23 | 0 | 0 | 0 | DOWCAL™ 10/DOWTHERM™ 10 Product Information Sheet, Dec 2009
DOWCAL™ 10/DOWTHERM™ 10 - 40 vol% | Dow Chemical | Ethylene glycol with inhibitor package | -20 | 170 |  |  |  |  | -4.727 | 1202.5658 | -83.1814 | -0.72116 | 1073.6624 | 0.00028253 | 0.42186 | 0.003258 | 3.4395 | [5 empty] | 0 | 25 | 50 | 100 | 150 | 170 | 1065 | 1056 | 1044 | 1011 | 965 | 944 | 3.44 | 3.52 | 3.6 | 3.77 | 3.93 | 3.99 | 0.404 | 0.43 | 0.449 | 0.469 | 0.464 | 0.455 | 5.41 | 2.38 | 1.31 | 0.56 | 0.31 | 0.25 | 0 | 0 | 0 | DOWCAL™ 10/DOWTHERM™ 10 Product Information Sheet, Dec 2009 |  |  | Liquid |  | Thermal |  | Vapor
DOWCAL™ 10/DOWTHERM™ 10 - 50 vol% | Dow Chemical | Ethylene glycol with inhibitor package | -35 | 170 |  |  |  |  | -5.2913 | 1555.1265 | -56.1414 | -0.74828 | 1087.0668 | 0.00025024 | 0.38886 | 0.0037657 | 3.2527 | [5 empty] | 0 | 25 | 50 | 100 | 150 | 170 | 1078 | 1069 | 1056 | 1022 | 975 | 952 | 3.25 | 3.35 | 3.44 | 3.63 | 3.82 | 3.89 | 0.374 | 0.396 | 0.412 | 0.43 | 0.426 | 0.419 | 7.21 | 3.11 | 1.68 | 0.68 | 0.35 | 0.28 | 0 | 0 | 0 | DOWCAL™ 10/DOWTHERM™ 10 Product Information Sheet, Dec 2009 |  | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure
DOWCAL™ 20/DOWFROST™ 20 - 30 vol% | Dow Chemical | Propylene glycol with inhibitor package | 0 | 170 |  |  |  |  | -2.8678 | 390.4369 | -193.6138 | -0.74308 | 1043.9217 | 0.0003067 | 0.44973 | 0.0026892 | 3.8099 | [5 empty] | 0 | 25 | 50 | 100 | 130 | 160 | 1036 | 1026 | 1013 | 977 | 949 | 917 | 3.81 | 3.88 | 3.94 | 4.08 | 4.16 | 4.24 | 0.431 | 0.459 | 0.479 | 0.499 | 0.494 | 0.479 | 6.19 | 2.38 | 1.2 | 0.5 | 0.37 | 0.29 | 0 | 0 | 0 | DOWCAL™ 20/DOWFROST™ Product Information Sheet, Jan 2008 |  | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg
DOWCAL™ 20/DOWFROST™ 20 - 40 vol% | Dow Chemical | Propylene glycol with inhibitor package | -15 | 170 |  |  |  |  | -2.2013 | 260.5828 | -221.9387 | -0.7986 | 1053.0579 | 0.00022042 | 0.41042 | 0.0032559 | 3.6593 | [5 empty] | 0 | 25 | 50 | 100 | 130 | 160 | 1045 | 1034 | 1019 | 981 | 951 | 917 | 3.66 | 3.74 | 3.82 | 3.99 | 4.08 | 4.18 | 0.395 | 0.417 | 0.433 | 0.448 | 0.443 | 0.429 | 11 | 3.38 | 1.53 | 0.62 | 0.46 | 0.38 | 0 | 0 | 0 | DOWCAL™ 20/DOWFROST™ Product Information Sheet, Jan 2008 |  | -10 | 827.3 | 0.51 | 0.089 | 4.7
DOWCAL™ 20/DOWFROST™ 20 - 50 vol% | Dow Chemical | Propylene glycol with inhibitor package | -30 | 170 |  |  |  |  | -2.6653 | 403.3088 | -202.5626 | -0.84174 | 1060.7345 | 0.00014614 | 0.37351 | 0.0038111 | 3.488 | [5 empty] | 0 | 25 | 50 | 100 | 130 | 160 | 1053 | 1040 | 1025 | 984 | 953 | 918 | 3.49 | 3.58 | 3.68 | 3.87 | 3.98 | 4.1 | 0.361 | 0.378 | 0.39 | 0.401 | 0.396 | 0.383 | 15.57 | 4.73 | 2.07 | 0.74 | 0.51 | 0.4 | 0 | 0 | 0 | DOWCAL™ 20/DOWFROST™ Product Information Sheet, Jan 2008 |  | 0 | 819.4333 | 0.532 | 0.091 | 3.7 | 3.36
DOWCAL™ N/DOWFROST™ - 30 vol% | Dow Chemical | Propylene glycol with inhibitor package, food grade | -10 | 100 |  |  |  |  | -3.0825 | 464.3995 | -181.185 | -0.64371 | 1040.8621 | 0.00052758 | 0.4398 | 0.0026597 | 3.8127 | [5 empty] | 0 | 25 | 50 | 75 | 100 | 120 | 1036 | 1026 | 1013 | 996 | 977 | 959 | 3.81 | 3.88 | 3.95 | 4.01 | 4.08 | 4.13 | 0.428 | 0.456 | 0.476 | 0.489 | 0.493 | 0.492 | 6.43 | 2.43 | 2.22 | 0.74 | 0.51 | 0.41 | 0 | 0 | 0 | DOWCAL™ N/DOWFROST™ Product Information Sheet, Mar 2007 |  | 20 | 803.7 | 0.58 | 0.093 | 2.35 |  |  | 15 | 1264.15 |  | 60 | 1136.555
DOWCAL™ N/DOWFROST™ - 40 vol% | Dow Chemical | Propylene glycol with inhibitor package, food grade | -20 | 100 |  |  |  |  | -2.8701 | 429.3104 | -194.0917 | -0.69306 | 1049.9056 | 0.00039613 | 0.40074 | 0.0031774 | 3.6707 | [5 empty] | 0 | 25 | 50 | 75 | 100 | 120 | 1045 | 1034 | 1019 | 1002 | 981 | 962 | 3.67 | 3.75 | 3.83 | 3.91 | 3.99 | 4.05 | 0.391 | 0.413 | 0.429 | 0.438 | 0.441 | 0.439 | 11.4 | 3.51 | 1.59 | 0.92 | 0.62 | 0.49 | 0 | 0 | 0 | DOWCAL™ N/DOWFROST™ Product Information Sheet, Mar 2007 |  | 40 | 787.9667 | 0.628 | 0.095 | 1.5 | 51.9 |  | 20 | 1261.08 | 1293.347 | 80 | 1084.291
DOWCAL™ N/DOWFROST™ - 50 vol% | Dow Chemical | Propylene glycol with inhibitor package, food grade | -30 | 100 |  |  |  |  | -3.1808 | 558.8975 | -181.1314 | -0.73548 | 1056.8548 | 0.00027306 | 0.36499 | 0.0037403 | 3.4993 | [5 empty] | 0 | 25 | 50 | 75 | 100 | 120 | 1052 | 1040 | 1024 | 1005 | 984 | 964 | 3.5 | 3.59 | 3.69 | 3.78 | 3.87 | 3.95 | 0.357 | 0.374 | 0.385 | 0.392 | 0.393 | 0.39 | 16.33 | 4.93 | 2.14 | 1.18 | 0.76 | 0.58 | 0 | 0 | 0 | DOWCAL™ N/DOWFROST™ Product Information Sheet, Mar 2007 |  | 60 | 772.2333 | 0.672 | 0.097 | 1 |  |  | 25 | 1158.02 | -2.6132 | 100 | 1032.027
DOWFROST™ - 30 vol% | Dow Chemical | Propylene glycol with inhibitor package | -10 | 100 |  |  |  |  | -3.0452 | 463.8106 | -181.2322 | -0.65731 | 1042.7596 | 0.00049245 | 0.43525 | 0.0027473 | 3.7934 | [5 empty] | 10 | 10 | 40 | 65 | 90 | 120 | 1033.71 | 1033.71 | 1019.56 | 1004.26 | 985.77 | 959.35 | 3.821 | 3.821 | 3.903 | 3.972 | 4.041 | 4.123 | 0.4344 | 0.4344 | 0.4622 | 0.4771 | 0.4846 | 0.4838 | 4.5068 | 4.5068 | 1.6295 | 0.9144 | 0.604 | 0.4246 | 0 | 0 | 0 | DOWFROST™ Product Information Sheet, Nov 2001 |  | 80 | 756.5 | 0.72 | 0.099 | 0.7 | 380.14 |  | 30 | 1254.95 |  | 120 | 979.763
DOWFROST™ - 40 vol% | Dow Chemical | Propylene glycol with inhibitor package | -20 | 100 |  |  |  |  | -2.9578 | 466.7385 | -188.5593 | -0.64887 | 1046.9626 | 0.00047406 | 0.38574 | 0.0033079 | 3.6352 | [5 empty] | -20 | 10 | 40 | 65 | 90 | 120 | 1053.16 | 1042.14 | 1026.49 | 1009.9 | 990.1 | 962.08 | 3.569 | 3.668 | 3.768 | 3.85 | 3.933 | 4.032 | 0.3635 | 0.3936 | 0.415 | 0.4262 | 0.4313 | 0.4294 | 48.9043 | 7.2173 | 2.2389 | 1.1762 | 0.7462 | 0.5084 | 0 | 0 | 0 | DOWFROST™ Product Information Sheet, Nov 2001 | [11 empty] | 140 | 927.499
DOWFROST™ - 50 vol% | Dow Chemical | Propylene glycol with inhibitor package | -30 | 100 |  |  |  |  | -3.4242 | 657.0851 | -167.9789 | -0.6577 | 1050.3615 | 0.00038574 | 0.34401 | 0.0038592 | 3.4548 | [5 empty] | -30 | -20 | 10 | 65 | 90 | 120 | 1064.83 | 1061.71 | 1049.25 | 1014.4 | 993.42 | 964 | 3.339 | 3.378 | 3.493 | 3.706 | 3.802 | 3.918 | 0.3246 | 0.3336 | 0.356 | 0.3792 | 0.3821 | 0.3792 | 172.8273 | 73.0193 | 10.6481 | 1.5483 | 0.9339 | 0.6029 | 0 | 0 | 0 | DOWFROST™ Product Information Sheet, Nov 2001 | [11 empty] | 160 | 875.235
DOWFROST™ HD - 30 vol% | Dow Chemical | Propylene glycol with inhibitor package, dyed bright yellow | -10 | 100 |  |  |  |  | -3.0452 | 463.8106 | -181.2322 | -0.64224 | 1052.6151 | 0.00049245 | 0.43525 | 0.0028543 | 3.7273 | [5 empty] | 10 | 10 | 40 | 65 | 90 | 120 | 1043.85 | 1043.85 | 1029.85 | 1014.87 | 996.86 | 971.26 | 3.756 | 3.756 | 3.841 | 3.913 | 3.984 | 4.07 | 0.4344 | 0.4344 | 0.4622 | 0.4771 | 0.4846 | 0.4838 | 4.5068 | 4.5068 | 1.6295 | 0.9144 | 0.604 | 0.4246 | 0 | 0 | 0 | DOWFROST™ HD Product Information Sheet, Nov 2001
DOWFROST™ HD - 40 vol% | Dow Chemical | Propylene glycol with inhibitor package, dyed bright yellow | -20 | 100 |  |  |  |  | -2.9578 | 466.7385 | -188.5593 | -0.63582 | 1060.2174 | 0.00047406 | 0.38574 | 0.0036921 | 3.5268 | [5 empty] | -20 | 10 | 40 | 65 | 90 | 120 | 1066.76 | 1055.38 | 1039.77 | 1023.55 | 1004.39 | 977.53 | 3.453 | 3.564 | 3.674 | 3.767 | 3.859 | 3.97 | 0.3635 | 0.3936 | 0.415 | 0.4262 | 0.4313 | 0.4294 | 48.9043 | 7.2173 | 2.2389 | 1.1762 | 0.7462 | 0.5084 | 0 | 0 | 0 | DOWFROST™ HD Product Information Sheet, Nov 2001
DOWFROST™ HD - 50 vol% | Dow Chemical | Propylene glycol with inhibitor package, dyed bright yellow | -30 | 100 |  |  |  |  | -3.4242 | 657.0851 | -167.9789 | -0.64961 | 1067.1032 | 0.00038574 | 0.34401 | 0.0045187 | 3.3005 | [5 empty] | -30 | -20 | 10 | 65 | 90 | 120 | 1081.98 | 1078.51 | 1065.4 | 1030.83 | 1010.61 | 982.63 | 3.165 | 3.21 | 3.346 | 3.594 | 3.707 | 3.843 | 0.3246 | 0.3336 | 0.356 | 0.3792 | 0.3821 | 0.3792 | 172.8273 | 73.0193 | 10.6481 | 1.5483 | 0.9339 | 0.6029 | 0 | 0 | 0 | DOWFROST™ HD Product Information Sheet, Nov 2001
DOWTHERM™ 4000 - 30 Vol% | Dow Chemical | Ethylene glycol with inhibitors, dyed fluorescent orange | -10 | 120 |  |  |  |  | -3.9934 | 832.5662 | -119.0838 | -0.58425 | 1064.7496 | 0.00069474 | 0.43474 | 0.0028907 | 3.5711 | [5 empty] | -10 | 10 | 40 | 65 | 90 | 120 | 1067.26 | 1058.99 | 1044.22 | 1029.74 | 1013.29 | 990.96 | 3.542 | 3.6 | 3.687 | 3.759 | 3.831 | 3.918 | 0.4154 | 0.442 | 0.4731 | 0.4909 | 0.5015 | 0.5044 | 6.1788 | 2.9482 | 1.3398 | 0.8246 | 0.5599 | 0.3846 | 0 | 0 | 0 | Dow, DOWTHERM™ 4000 Product Information Sheet, Nov 2001
DOWTHERM™ 4000 - 40 Vol% | Dow Chemical | Ethylene glycol with inhibitors, dyed fluorescent orange | -20 | 120 |  |  |  |  | -4.4124 | 1071.2011 | -98.7746 | -0.60821 | 1080.9775 | 0.00062781 | 0.39589 | 0.0034278 | 3.3754 | [5 empty] | -20 | 10 | 40 | 65 | 90 | 120 | 1089.06 | 1075.9 | 1059.95 | 1044.52 | 1027.16 | 1003.77 | 3.307 | 3.41 | 3.512 | 3.598 | 3.684 | 3.787 | 0.3707 | 0.4053 | 0.4312 | 0.4462 | 0.4552 | 0.4582 | 15.7533 | 4.0451 | 1.7731 | 1.0646 | 0.7013 | 0.4614 | 0 | 0 | 0 | Dow, DOWTHERM™ 4000 Product Information Sheet, Nov 2001
DOWTHERM™ 4000 - 50 Vol% | Dow Chemical | Ethylene glycol with inhibitors, dyed fluorescent orange | -30 | 120 |  |  |  |  | -4.2503 | 991.8804 | -118.1087 | -0.61823 | 1094.5425 | 0.00057845 | 0.35848 | 0.0039543 | 3.1698 | [5 empty] | -30 | -20 | 10 | 65 | 90 | 120 | 1109.98 | 1105.84 | 1091.59 | 1058.37 | 1040.23 | 1015.96 | 3.051 | 3.091 | 3.209 | 3.427 | 3.526 | 3.644 | 0.3333 | 0.3442 | 0.3724 | 0.4062 | 0.4139 | 0.4168 | 43.997 | 22.0816 | 5.5071 | 1.2936 | 0.8227 | 0.5252 | 0 | 0 | 0 | Dow, DOWTHERM™ 4000 Product Information Sheet, Nov 2001
DOWTHERM™ A | Dow Chemical | Biphenyl and diphenyl oxide eutectic mixture - liquid phase properties | 15 | 400 |  | 8.729 | 3828.1054 | 392.5107 | -5.485 | 2637.3596 | 105.6665 | -0.98935 | 1091.5087 | -0.00016 | 0.1419 | 0.0029467 | 1.5009 | 113 | 257 | Biphynyl, Diphenyl Oxide |  |  | 15 | 65 | 155 | 205 | 305 | 405 | 1063.5 | 1023.7 | 947.8 | 902.5 | 801.3 | 672.5 | 1.558 | 1.701 | 1.954 | 2.083 | 2.373 | 2.725 | 0.1395 | 0.1315 | 0.1171 | 0.1091 | 0.0931 | 0.0771 | 5 | 1.58 | 0.56 | 0.38 | 0.2 | 0.12 | 2.3 | 210 | 8490 | Dow, DOWTHERM™ A Product Information Sheet, Nov 2001
DOWTHERM™ G | Dow Chemical | Di- and tri-aryl compounds mixture | -6 | 360 |  | 28.1431 | 70966.9119 | 2506.6472 | -4.2087 | 1446.7466 | -80.3559 | -0.77472 | 1062.346 | -0.0001158 | 0.12872 | 0.0034971 | 1.4756 | 280 | 552 | Di- and Tr-aryl Ethers |  |  | -5 | 15 | 115 | 195 | 275 | 375 | 1066.2 | 1050.7 | 973.3 | 911.3 | 849.3 | 771.8 | 1.458 | 1.528 | 1.878 | 2.158 | 2.437 | 2.787 | 0.1293 | 0.127 | 0.1154 | 0.1061 | 0.0969 | 0.0853 | 55.9 | 15.7 | 1.45 | 0.62 | 0.34 | 0.19 | 1 | 75 | 3280 | Dow, DOWTHERM™ G Product Information Sheet, Dec 2001
DOWTHERM™ J | Dow Chemical | Mixture of isomers of an alkylated aromatic | -80 | 315 |  | 59.0974 | 290462.7583 | 4950.074 | -3.0706 | 638.5207 | -77.404 | -0.91494 | 873.6791 | -0.00021071 | 0.13232 | 0.0036267 | 1.804 | 57 | 181 | Alkylated Aromatic |  |  | -80 | -60 | 0 | 80 | 160 | 320 | 931.3 | 921 | 878.5 | 817.4 | 749.2 | 560.4 | 1.584 | 1.616 | 1.769 | 2.023 | 2.315 | 3.04 | 0.1485 | 0.1453 | 0.1326 | 0.1156 | 0.0987 | 0.0647 | 8.43 | 5.12 | 1.23 | 0.47 | 0.28 | 0.16 | 0.5 | 22.5 | 9592 | Dow, DOWTHERM™ J Product Information Sheet, Nov 2001
DOWTHERM™ MX | Dow Chemical | Mixture of alkylated aromatics | -20 | 330 |  | -416.7584 | 15972101.997 | -38392.3121 | -4.547 | 1505.7682 | -91.4517 | -0.77586 | 979.0294 | -0.00010507 | 0.12503 | 0.00325 | 1.545 | 165 | 328 |  |  |  | -20 | 40 | 160 | 220 | 280 | 340 | 989.8 | 948.2 | 860.4 | 813.2 | 763 | 708.2 | 1.48 | 1.675 | 2.065 | 2.26 | 2.455 | 2.65 | 0.127 | 0.121 | 0.108 | 0.102 | 0.096 | 0.089 | 213.9 | 9.44 | 0.85 | 0.45 | 0.28 | 0.19 | 0.5 | 46 | 960 | Dow, DOWTHERM™ MX Product Information Sheet, Nov 2001
DOWTHERM™ Q | Dow Chemical | Mixture of diphenylethane and alkylated aromatics | -35 | 330 |  | 25.6353 | 53251.6069 | 2053.164 | -3.3915 | 743.0916 | -135.9068 | -0.76282 | 982.128 | -0.00014873 | 0.12424 | 0.0030301 | 1.5928 | 120 | 267 | Diphenylethane, Alkylated Aromatic |  |  | -35 | 0 | 80 | 160 | 240 | 360 | 1011.4 | 980.5 | 920 | 859.5 | 799 | 708.3 | 1.478 | 1.589 | 1.842 | 2.088 | 2.327 | 2.672 | 0.128 | 0.1244 | 0.1143 | 0.1028 | 0.0843 | 0.0719 | 46.6 | 7.56 | 1.07 | 0.41 | 0.24 | 0.15 | 0.5 | 37.5 | 3700 | Dow, DOWTHERM™ Q Product Information Sheet, Nov 2001
DOWTHERM™ RP | Dow Chemical | Synthetic diaryl alkyl liquid | 10 | 350 |  | -15.6439 | 25860.1396 | -1755.4799 | -3.199 | 983.1702 | -141.8282 | -0.74345 | 1046.4705 | -0.00012967 | 0.13397 | 0.0029748 | 1.561 | 194 | 353 |  |  |  | 10 | 70 | 130 | 190 | 310 | 370 | 1036.2 | 994.2 | 951.7 | 908.3 | 817.4 | 768.1 | 1.591 | 1.769 | 1.948 | 2.126 | 2.483 | 2.662 | 0.1327 | 0.1249 | 0.1171 | 0.1093 | 0.0938 | 0.086 | 88.17 | 5.39 | 1.71 | 0.87 | 0.38 | 0.29 | 0.5 | 7.5 | 1050 | Dow, DOWTHERM™ RP Product Information Sheet, Nov 2001
DOWTHERM™ SR-1 - 30 Vol% | Dow Chemical | Ethylene glycol with inhibitors, dyed fluorescent pink | -10 | 120 |  |  |  |  | -3.9934 | 832.5662 | -119.0838 | -0.54151 | 1055.1995 | 0.00069474 | 0.43474 | 0.0028382 | 3.5905 | [5 empty] | -10 | 10 | 40 | 65 | 90 | 120 | 1055.47 | 1049.91 | 1037.92 | 1024.59 | 1008.2 | 984.53 | 3.562 | 3.619 | 3.704 | 3.775 | 3.846 | 3.931 | 0.4154 | 0.442 | 0.4731 | 0.4909 | 0.5015 | 0.5044 | 6.1788 | 2.9482 | 1.3398 | 0.8246 | 0.5599 | 0.3846 | 0 | 0 | 0 | Dow, DOWTHERM™ SR-1 Product Information Sheet, Jun 2002
DOWTHERM™ SR-1 - 40 Vol% | Dow Chemical | Ethylene glycol with inhibitors, dyed fluorescent pink | -20 | 120 |  |  |  |  | -4.4124 | 1071.2011 | -98.7746 | -0.54963 | 1068.6496 | 0.00062781 | 0.39589 | 0.0033533 | 3.4029 | [5 empty] | -20 | 10 | 40 | 65 | 90 | 120 | 1073.23 | 1064.73 | 1051.85 | 1037.76 | 1020.63 | 996.06 | 3.336 | 3.436 | 3.537 | 3.621 | 3.705 | 3.805 | 0.3707 | 0.4053 | 0.4312 | 0.4462 | 0.4552 | 0.4582 | 15.7533 | 4.0451 | 1.7731 | 1.0646 | 0.7013 | 0.4614 | 0 | 0 | 0 | Dow, DOWTHERM™ SR-1 Product Information Sheet, Jun 2002
DOWTHERM™ SR-1 - 50 Vol% | Dow Chemical | Ethylene glycol with inhibitors, dyed fluorescent pink | -30 | 120 |  |  |  |  | -4.2503 | 991.8804 | -118.1087 | -0.54397 | 1078.9789 | 0.00057845 | 0.35848 | 0.0038647 | 3.2061 | [5 empty] | -30 | -20 | 10 | 65 | 90 | 120 | 1090.31 | 1088.15 | 1078.72 | 1050.05 | 1032.15 | 1006.66 | 3.09 | 3.129 | 3.245 | 3.457 | 3.554 | 3.67 | 0.3333 | 0.3442 | 0.3724 | 0.4062 | 0.4139 | 0.4168 | 43.997 | 22.0816 | 5.5071 | 1.2936 | 0.8227 | 0.5252 | 0 | 0 | 0 | Dow, DOWTHERM™ SR-1 Product Information Sheet, Jun 2002
DOWTHERM™ T | Dow Chemical | Mixture of C14-C30 alkyl benzenes | -10 | 288 |  | 20.3132 | 24800.7847 | 1071.4836 | -3.3717 | 1025.6706 | -139.9293 | -0.68914 | 887.0438 | -0.00022073 | 0.13885 | 0.0029811 | 1.9027 | 188 | 345 |  |  |  | -10 | 40 | 140 | 190 | 290 | 320 | 893.9 | 859.5 | 790.6 | 756.1 | 687.2 | 666.5 | 1.873 | 2.022 | 2.32 | 2.469 | 2.767 | 2.857 | 0.141 | 0.13 | 0.108 | 0.097 | 0.075 | 0.068 | 251.68 | 12.8 | 1.45 | 0.82 | 0.39 | 0.33 | 0.01 | 4.5 | 309 | Dow, DOWTHERM™ T Product Information Sheet, Apr 2004
DURATHERM 450 | Duratherm, division of Frontier Resource & Recovery Services | Refined oil, non-aromatic | 0 | 230 |  | -6.6505 | 8198.9412 | -1156.007 | -2.7476 | 674.268 | -150.9507 | -0.67777 | 874.5009 | -7.5284e-05 | 0.14496 | 0.0030161 | 2.0209 | 150 | 250 | Paraffinic |  |  | -1 | 49 | 99 | 149 | 199 | 232 | 877.01 | 842.89 | 800.92 | 774.81 | 740.69 | 717.95 | 2.018 | 2.169 | 2.319 | 2.47 | 2.621 | 2.721 | 0.145 | 0.142 | 0.137 | 0.133 | 0.13 | 0.128 | 18.59 | 3.29 | 1.36 | 0.77 | 0.52 | 0.43 | 5.7 | 31 | 167 | Duratherm 450 Data Sheet, 2010
DURATHERM 600 | Duratherm, division of Frontier Resource & Recovery Services | Refined and hydrotreated paraffinic oils, non-toxic and non-reportable | 0 | 315 |  | -7.6661 | 5665.649 | -900.1096 | -2.9062 | 903.5619 | -168.874 | -0.67434 | 866.3945 | -5.0688e-05 | 0.14317 | 0.0032986 | 1.8383 | 224 | 380 | Paraffinic |  |  | -20 | 10 | 80 | 160 | 240 | 320 | 879.86 | 859.64 | 812.48 | 758.52 | 704.55 | 650.59 | 1.772 | 1.872 | 2.103 | 2.363 | 2.633 | 2.893 | 0.144 | 0.143 | 0.139 | 0.135 | 0.131 | 0.127 | 2691 | 148.51 | 7.05 | 1.67 | 0.76 | 0.46 | 0.05 | 0.975 | 126 | Duratherm 600 Data Sheet, 2010
DURATHERM 630 | Duratherm, division of Frontier Resource & Recovery Services | Refined and hydrotreated paraffinic oils, non-toxic and non-reportable | 20 | 332 |  | 24.8347 | 45060.3451 | 1649.0921 | -2.9927 | 972.3144 | -160.4413 | -0.67296 | 870.1405 | -5.2943e-05 | 0.14384 | 0.0032794 | 1.8447 | 229 | 380 | Paraffinic |  |  | 15 | 75 | 145 | 205 | 265 | 335 | 860.04 | 819.69 | 772.53 | 732.18 | 691.84 | 644.68 | 1.892 | 2.093 | 2.323 | 2.513 | 2.714 | 2.944 | 0.143 | 0.14 | 0.136 | 0.133 | 0.13 | 0.126 | 123.54 | 8.91 | 2.17 | 1.07 | 0.66 | 0.44 | 0.05 | 3.4 | 133 | Duratherm 630 Data Sheet, 2010
DURATHERM FG | Duratherm, division of Frontier Resource & Recovery Services | Refined paraffinic oils with additives, food grade | 20 | 332 |  | 24.8347 | 45060.3451 | 1649.0921 | -2.9927 | 972.3144 | -160.4413 | -0.67296 | 870.1405 | -5.2943e-05 | 0.14384 | 0.0032794 | 1.8447 | 227 | 410 | Paraffinic |  |  | 15 | 75 | 145 | 205 | 265 | 335 | 860.04 | 819.69 | 772.53 | 732.18 | 691.84 | 644.68 | 1.892 | 2.093 | 2.323 | 2.513 | 2.714 | 2.944 | 0.143 | 0.14 | 0.136 | 0.133 | 0.13 | 0.126 | 123.54 | 8.91 | 2.17 | 1.07 | 0.66 | 0.44 | 0.05 | 3.4 | 133 | Duratherm FG Data Sheet, 2010
DURATHERM G | Duratherm, division of Frontier Resource & Recovery Services | Polyalkylene glycol based fluid with additives | 20 | 260 |  | 2.1359 | 189.0776 | 17.0139 | -2.1332 | 859.9469 | -168.1963 | -0.54571 | 938.1532 | -0.00014979 | 0.16988 | 0.0018019 | 1.9064 | 267 | 370 | Polyalkylene Glycol |  |  | 10 | 38 | 93 | 143 | 199 | 260 | 931 | 915 | 888.01 | 863.72 | 836.73 | 789 | 1.913 | 1.968 | 2.079 | 2.18 | 2.292 | 2.345 | 0.169 | 0.164 | 0.156 | 0.148 | 0.139 | 0.132 | 220.78 | 48.54 | 8.91 | 3.8 | 2.05 | 1.25 | 0.05 | 9 | 28.4 | Duratherm G Data Sheet, 2010
DURATHERM Lite | Duratherm, division of Frontier Resource & Recovery Services | Same as Duratherm 600, but with fewer additives | 0 | 315 |  | -7.6661 | 5665.649 | -900.1096 | -2.9062 | 903.5619 | -168.874 | -0.67434 | 866.3945 | -5.0688e-05 | 0.14317 | 0.0032986 | 1.8383 | 224 | 380 |  |  |  | -20 | 10 | 80 | 160 | 240 | 320 | 879.86 | 859.64 | 812.48 | 758.52 | 704.55 | 650.59 | 1.772 | 1.872 | 2.103 | 2.363 | 2.633 | 2.893 | 0.144 | 0.143 | 0.139 | 0.135 | 0.131 | 0.127 | 2691 | 148.51 | 7.05 | 1.67 | 0.76 | 0.46 | 0.05 | 0.975 | 126 | Duratherm Lite Data Sheet, 2010
DURATHERM LT | Duratherm, division of Frontier Resource & Recovery Services | Refined oil, non-aromatic | -35 | 315 |  | 14.9056 | 16265.9291 | 1013.6574 | -3.0148 | 794.6464 | -152.1293 | -0.68416 | 827.0379 | -8.5018e-05 | 0.14264 | 0.0034339 | 2.0187 | 165 | 325 | Paraffinic |  |  | -40 | -10 | 60 | 140 | 220 | 310 | 854.13 | 833.71 | 786.05 | 731.68 | 677.22 | 614.21 | 1.882 | 1.983 | 2.223 | 2.503 | 2.774 | 3.082 | 0.146 | 0.143 | 0.138 | 0.131 | 0.124 | 0.116 | 999.67 | 62.98 | 3.73 | 1.03 | 0.52 | 0.31 | 0.05 | 6.4 | 414 | Duratherm LT Data Sheet, 2010
DURATHERM S | Duratherm, division of Frontier Resource & Recovery Services | Refined oil, non-aromatic especially resistant to oxidation | -40 | 340 |  | 2.6299 | 181.8693 | 58.2658 | -3.8294 | 3727.4502 | 178.4719 | -0.46997 | 976.7419 | -0.00020107 | 0.13602 | 0.001703 | 1.6287 | 323 | 500 | Silicone |  |  | -40 | -12 | 60 | 138 | 221 | 310 | 997.36 | 982.38 | 947.43 | 909.98 | 872.54 | 832.59 | 1.561 | 1.614 | 1.724 | 1.862 | 2.005 | 2.159 | 0.144 | 0.138 | 0.125 | 0.108 | 0.091 | 0.074 | 287.03 | 104.52 | 28.77 | 12.09 | 6.34 | 2.9 | 0.05 | 50.5 | 136.8 | Duratherm S Data Sheet, 2010
DURATHERM XLT-120 | Duratherm, division of Frontier Resource & Recovery Services | Refined silocone oil, for cryogenic applications, food & pharma | -84 | 65 |  | -3.0112 | 165.7661 | -95.9293 | -1.9216 | 442.3148 | -120.7874 | -0.49886 | 847.4328 | -6.5331e-05 | 0.13574 | 0.0021834 | 2.0208 | 98.8 | 500 |  |  |  | -84 | -68 | -29 | -1 | 32 | 65 | 889 | 881 | 862 | 849 | 832 | 814 | 1.842 | 1.879 | 1.95 | 2.01 | 2.081 | 2.177 | 0.141 | 0.14 | 0.138 | 0.136 | 0.134 | 0.131 | 70.28 | 27.7 | 5.19 | 2.72 | 1.62 | 1.12 | 0.01 | 0.05 | 223 | Duratherm XLT-120 Data Sheet, 2010
DURATHERM XLT-50 | Duratherm, division of Frontier Resource & Recovery Services | Refined silocone oil, for cryogenic applications, food & pharma | -46 | 176 |  | 5.5776 | 1026.1685 | 178.1814 | -2.661 | 567.1765 | -137.0065 | -0.96414 | 848.4502 | -9.7898e-05 | 0.1356 | 0.0026614 | 2.0187 | 98.8 | 500 |  |  |  | -40 | -29 | 38 | 77 | 121 | 176 | 868 | 863 | 830 | 808 | 750 | 641 | 1.926 | 1.95 | 2.093 | 2.211 | 2.345 | 2.5 | 0.138 | 0.138 | 0.133 | 0.13 | 0.125 | 0.116 | 59.49 | 13.91 | 1.51 | 1 | 0.68 | 0.43 | 0.05 | 36 | 479 | Duratherm XLT-50 Data Sheet, 2010
Dynalene® 600 | Dynalene | Silicone-based product with enhanced resistance to oxidation | 70 | 288 |  |  |  |  | -1.9727 | 2181.1961 | 29.0849 | -1 | 983 | -0.00017733 | 0.15747 | 0.0018853 | 1.2342 | 315 | 315 |  |  |  | 70 | 100 | 130 | 170 | 230 | 288 | 913 | 883 | 853 | 813 | 753 | 695 | 1.366 | 1.423 | 1.479 | 1.555 | 1.668 | 1.777 | 0.1451 | 0.1397 | 0.1344 | 0.1273 | 0.1167 | 0.1064 | 48.6 | 31.5 | 21.6 | 14.1 | 8.4 | 5.6 | 0 | 0 | 0 | Dynalene 600 Data Sheet, 2010
Dynalene® BioGlycol - 20 Vol% | Dynalene | Produced from corn, better performance than propylene glycol | -6.6667 | 115.5556 |  |  |  |  | -2.8391 | 403.139 | -179.0402 | -0.56057 | 1029.826 | 0.00075301 | 0.47277 | 0.0058246 | 4.0083 | [5 empty] | -6.6667 | 10 | 37.7778 | 60 | 82.2222 | 115.5556 | 1028.8657 | 1023.9 | 1012.3667 | 1000.513 | 986.0964 | 959.6659 | 3.9775 | 4.0612 | 4.2287 | 4.3543 | 4.4799 | 4.6892 | 0.45345 | 0.47941 | 0.51057 | 0.5348 | 0.53999 | 0.54345 | 5.07 | 2.81 | 1.28 | 0.8 | 0.57 | 0.4 | 0 | 0 | 0 | Dynalene BioGlycol Data Sheet, 2010
Dynalene® BioGlycol - 40 Vol% | Dynalene | Produced from corn, better performance than propylene glycol | -17.7778 | 115.5556 |  |  |  |  | -1.7621 | 259.4531 | -209.4499 | -0.64191 | 1046.8234 | 0.00049314 | 0.38494 | 0.005872 | 3.6308 | [5 empty] | -17.7778 | -1.1111 | 26.6667 | 48.8889 | 82.2222 | 115.5556 | 1052.573 | 1046.8064 | 1033.9916 | 1021.0166 | 996.6686 | 966.5539 | 3.5169 | 3.6425 | 3.7681 | 3.9356 | 4.1031 | 4.3124 | 0.36519 | 0.38422 | 0.40672 | 0.41711 | 0.43095 | 0.43095 | 24.31 | 10.84 | 3.38 | 1.72 | 0.93 | 0.73 | 0 | 0 | 0 | Dynalene BioGlycol Data Sheet, 2010
Dynalene® BioGlycol - 60 Vol% | Dynalene | Produced from corn, better performance than propylene glycol | -28.8889 | 115.5556 |  |  |  |  | -2.1274 | 490.7649 | -175.4512 | -0.7077 | 1058.2805 | 0.00023357 | 0.31461 | 0.0057936 | 3.2583 | [5 empty] | -28.8889 | -12.2222 | 15.5556 | 37.7778 | 82.2222 | 115.5556 | 1072.1155 | 1065.8683 | 1052.0925 | 1038.1564 | 1002.9158 | 969.9178 | 3.0982 | 3.182 | 3.3494 | 3.475 | 3.7263 | 3.9356 | 0.30115 | 0.3098 | 0.32365 | 0.33057 | 0.33749 | 0.33403 | 146 | 37.12 | 10.57 | 4.46 | 1.5 | 1.19 | 0 | 0 | 0 | Dynalene BioGlycol Data Sheet, 2010
Dynalene® EG - 20 Vol% | Dynalene | Inhibited ethylene glycol | -6.6667 | 121.1111 |  |  |  |  | -3.5193 | 637.3661 | -135.0373 | -0.52459 | 1045.9286 | 0.00089095 | 0.47398 | 0.0023333 | 3.7589 | [5 empty] | -6.6667 | 4.4444 | 21.1111 | 37.7778 | 60 | 104.4444 | 1046.9665 | 1042.8017 | 1036.074 | 1028.3851 | 1016.6917 | 988.6594 | 3.743 | 3.7681 | 3.81 | 3.8477 | 3.8979 | 4.0026 | 0.45691 | 0.47422 | 0.49845 | 0.51749 | 0.53826 | 0.55557 | 3.9 | 2.59 | 1.61 | 1.11 | 0.74 | 0.41 | 0 | 0 | 0 | Dynalene EG Data Sheet
Dynalene® EG - 40 Vol% | Dynalene | Inhibited ethylene glycol | -17.7778 | 121.1111 |  |  |  |  | -3.9284 | 860.2757 | -122.0346 | -0.58864 | 1080.8533 | 0.00069453 | 0.39517 | 0.0034264 | 3.3757 | [5 empty] | -17.7778 | -1.1111 | 21.1111 | 37.7778 | 60 | 104.4444 | 1088.134 | 1081.0859 | 1070.3535 | 1061.223 | 1047.7675 | 1016.2111 | 3.3159 | 3.3704 | 3.4499 | 3.5044 | 3.5797 | 3.7346 | 0.37384 | 0.39288 | 0.41538 | 0.42922 | 0.44307 | 0.45864 | 13.76 | 6.09 | 2.87 | 1.87 | 1.17 | 0.57 | 0 | 0 | 0 | Dynalene EG Data Sheet
Dynalene® EG - 60 Vol% | Dynalene | Inhibited ethylene glycol | -34.4444 | 121.1111 |  |  |  |  | -4.399 | 1040.0874 | -122.0768 | -0.62349 | 1109.9764 | 0.00051821 | 0.33281 | 0.0044667 | 2.9533 | [5 empty] | -34.4444 | -17.7778 | 10 | 32.2222 | 60 | 104.4444 | 1127.6996 | 1120.3311 | 1106.5552 | 1093.2599 | 1074.8387 | 1040.8795 | 2.801 | 2.8721 | 2.9977 | 3.0982 | 3.2196 | 3.4206 | 0.30807 | 0.32192 | 0.34269 | 0.35653 | 0.36865 | 0.37903 | 89.67 | 30.08 | 7.85 | 3.58 | 1.69 | 0.72 | 0 | 0 | 0 | Dynalene EG Data Sheet
Dynalene® HC-10 | Dynalene | Aqueous-based, engineered for low temperature applications | -10 | 60 |  |  |  |  | -4.2758 | 1294.1517 | -23.895 | -0.6913 | 1363.1739 | 0.001 | 0.505 | 0.003 | 3.28 | [5 empty] | -10 | 0 | 10 | 20 | 40 | 50 | 1370 | 1364 | 1358 | 1346 | 1335 | 1330 | 3.25 | 3.28 | 3.31 | 3.34 | 3.4 | 3.43 | 0.495 | 0.505 | 0.515 | 0.525 | 0.545 | 0.555 | 3 | 2.5 | 2.05 | 1.7 | 1.2 | 1.05 | 0 | 0 | 0 | Dynalene HC Engineering Guide
Dynalene® HC-20 | Dynalene | Aqueous-based, engineered for low temperature applications | -20 | 60 |  |  |  |  | -5.2911 | 2948.8383 | 163.736 | -0.498 | 1248.8 | 0.000954 | 0.5021 | 0.00228 | 3.177 | [5 empty] | -20 | 0 | 10 | 20 | 40 | 50 | 1259 | 1249 | 1244 | 1238 | 1228 | 1225 | 3.13 | 3.18 | 3.2 | 3.22 | 3.27 | 3.29 | 0.483 | 0.502 | 0.512 | 0.521 | 0.54 | 0.55 | 6 | 4.3 | 3.6 | 3.2 | 2.4 | 2.15 | 0 | 0 | 0 | Dynalene HC Engineering Guide
Dynalene® HC-30 | Dynalene | Aqueous-based, engineered for low temperature applications | -30 | 60 |  |  |  |  | -0.51228 | 242.6453 | -157.8371 | -0.59559 | 1282.9412 | 0.0011 | 0.498 | 0.0026912 | 3.0191 | [5 empty] | -30 | -10 | 10 | 20 | 40 | 50 | 1305 | 1285 | 1275 | 1270 | 1260 | 1255 | 2.94 | 2.99 | 3.04 | 3.08 | 3.13 | 3.15 | 0.465 | 0.487 | 0.509 | 0.52 | 0.542 | 0.553 | 8.3 | 6 | 4.1 | 3.6 | 2.9 | 2.6 | 0 | 0 | 0 | Dynalene HC Engineering Guide
Dynalene® HC-40 | Dynalene | Aqueous-based, engineered for low temperature applications | -40 | 60 |  |  |  |  | -2.9869 | 974.8234 | -58.2554 | -0.7 | 1330 | 0.0009875 | 0.4895 | 0.0023 | 2.89 | [5 empty] | -40 | -20 | 0 | 20 | 40 | 50 | 1358 | 1344 | 1330 | 1316 | 1302 | 1295 | 2.798 | 2.844 | 2.89 | 2.936 | 2.982 | 3.005 | 0.45 | 0.46975 | 0.4895 | 0.50925 | 0.529 | 0.53887 | 13 | 7.5 | 5 | 3.2 | 2.2 | 2 | 0 | 0 | 0 | Dynalene HC Engineering Guide
Dynalene® HC-50 | Dynalene | Aqueous-based, engineered for low temperature applications | -50 | 60 |  |  |  |  | -8.6842 | 4625.6444 | 162.8836 | -0.55 | 1362.5 | 0.00098 | 0.48433 | 0.002 | 2.67 | [5 empty] | -50 | -30 | -10 | 10 | 30 | 50 | 1390 | 1379 | 1368 | 1357 | 1346 | 1335 | 2.57 | 2.61 | 2.65 | 2.69 | 2.73 | 2.77 | 0.435 | 0.455 | 0.475 | 0.494 | 0.514 | 0.533 | 28 | 15 | 8.7 | 5.4 | 3.6 | 2.3 | 0 | 0 | 0 | Dynalene HC Engineering Guide
Dynalene® HF | Dynalene | Biodegradable aliphatic hydrocarbon blend, food grade | -80 | 162.7778 |  | 10.4702 | 4350.478 | 388.8686 | -11.0043 | 7574.1457 | 365.4554 | -0.70242 | 816.7797 | -0.00019755 | 0.12429 | 0.0045492 | 1.9236 | 61 | 175 |  |  |  | -62.2222 | -40 | 15.5556 | 60 | 104.4444 | 148.8889 | 860.1913 | 845.7747 | 805.7285 | 773.6916 | 743.2565 | 712.8215 | 1.6454 | 1.7375 | 1.9887 | 2.1981 | 2.4074 | 2.5958 | 0.135 | 0.13067 | 0.12288 | 0.11509 | 0.10731 | 0.089998 | 13 | 5.2 | 1.6 | 0.85 | 0.46 | 0.25 | 0.01 | 6 | 240 | Dynalene HF and Dynalene MV Engineering Guide
Dynalene® HF-LO | Dynalene | Aliphatic hydrocarbon blend, non-toxic, odorless | -73 | 177 |  |  |  |  | -3.8019 | 919.1524 | -81.3857 | -0.75982 | 777.6671 | -0.0002 | 0.1126 | 0.0038003 | 2.0191 | 61 | 191 |  |  |  | -73 | -60 | 0 | 50 | 110 | 177 | 833 | 823 | 778 | 740 | 694 | 643 | 1.742 | 1.791 | 2.019 | 2.209 | 2.437 | 2.692 | 0.1272 | 0.1246 | 0.1126 | 0.1026 | 0.0906 | 0.0772 | 70.2 | 23.9 | 2.5 | 1 | 0.49 | 0.27 | 0 | 0 | 0 | Dynalene HF-LO Data Sheet
Dynalene® HT | Dynalene | Synthetic organic hydrocaron | 20 | 177 |  |  |  |  | -3.3618 | 1050.8376 | -143.2 | -0.71592 | 1058.5096 | -0.00013187 | 0.13327 | 0.0037257 | 1.4747 | 200 | 385 |  |  |  | 20 | 40 | 100 | 160 | 220 | 280 | 1044 | 1030 | 987 | 944 | 901 | 858 | 1.549 | 1.624 | 1.847 | 2.071 | 2.294 | 2.518 | 0.1306 | 0.128 | 0.1201 | 0.1122 | 0.1043 | 0.0963 | 49 | 16.8 | 3.3 | 1.3 | 0.72 | 0.45 | 0 | 0 | 0 | Dynalene HT Data Sheet
Dynalene® LO-170 | Dynalene | Aliphatic hydrocarbon blend | -40 | 205 |  |  |  |  | -4.0091 | 975.0043 | -100.5306 | -0.50168 | 784.0074 | -0.0002 | 0.1165 | 0.0038 | 1.804 | 77 | 223 |  |  |  | -40 | -30 | 10 | 60 | 120 | 205 | 804 | 799 | 779 | 754 | 724 | 681 | 1.652 | 1.69 | 1.842 | 2.032 | 2.26 | 2.583 | 0.1245 | 0.1225 | 0.1145 | 0.1045 | 0.0925 | 0.0755 | 33.2 | 16.9 | 3.4 | 1.2 | 0.53 | 0.24 | 0 | 0 | 0 | Dynalene LO-170 Data Sheet
Dynalene® LO-230 | Dynalene | Aliphatic hydrocarbon blend | 0 | 205 |  |  |  |  | -3.1805 | 851.714 | -146.0126 | -0.69815 | 814.9279 | -0.0002 | 0.151 | 0.0038 | 1.934 | 110 | 273 |  |  |  | 0 | 10 | 50 | 90 | 150 | 205 | 815 | 808 | 780 | 752 | 710 | 672 | 1.934 | 1.972 | 2.124 | 2.276 | 2.504 | 2.713 | 0.151 | 0.149 | 0.141 | 0.133 | 0.121 | 0.11 | 34.1 | 20.7 | 5 | 2.1 | 0.92 | 0.54 | 0 | 0 | 0 | Dynalene LO-230 Data Sheet
Dynalene® MV | Dynalene | Biodegradable hydrocarbon blend | -112.2222 | 162.7778 |  | -27.8705 | 38860.6487 | -1417.6769 | -4.4953 | 1230.8755 | -17.8291 | -0.77262 | 860.8388 | -0.00023774 | 0.13761 | 0.0035417 | 1.7236 | 53 | 176 |  |  |  | -106.6667 | -84.4444 | -28.8889 | 15.5556 | 60 | 126.6667 | 943.4873 | 925.867 | 882.6171 | 848.9784 | 815.3396 | 762.4787 | 1.3481 | 1.4277 | 1.6119 | 1.7794 | 1.9385 | 2.1729 | 0.16269 | 0.15836 | 0.14365 | 0.13413 | 0.12375 | 0.10731 | 88 | 15 | 2 | 1.05 | 0.66 | 0.28 | 0.01 | 0.7 | 170 | Dynalene HF and Dynalene MV Engineering Guide
Dynalene® PG - 20 Vol% | Dynalene | Propylene glycol with corrosion inhibitors | -6.6667 | 121.1111 |  |  |  |  | -3.7439 | 656.3234 | -145.4857 | -0.53047 | 1028.418 | 0.00082817 | 0.46793 | 0.002197 | 3.9314 | [5 empty] | -6.6667 | -1.1111 | 15.5556 | 37.7778 | 71.1111 | 104.4444 | 1028.8657 | 1027.424 | 1021.8176 | 1012.3667 | 993.6251 | 969.1168 | 3.9188 | 3.9272 | 3.9649 | 4.0151 | 4.0863 | 4.1617 | 0.45345 | 0.46211 | 0.48634 | 0.51057 | 0.5348 | 0.54345 | 5.36 | 4.23 | 2.32 | 1.25 | 0.64 | 0.4 | 0 | 0 | 0 | Dynalene PG Data Sheet
Dynalene® PG - 40 Vol% | Dynalene | Propylene glycol with corrosion inhibitors | -6.6667 | 121.1111 |  |  |  |  | -4.0579 | 747.1473 | -159.3212 | -0.60831 | 1045.7626 | 0.00055256 | 0.38295 | 0.0032916 | 3.6377 | [5 empty] | -17.7778 | -12.2222 | 10 | 32.2222 | 60 | 104.4444 | 1052.573 | 1050.811 | 1042.161 | 1030.9481 | 1013.488 | 977.1261 | 3.5797 | 3.5965 | 3.6718 | 3.743 | 3.8351 | 3.9816 | 0.36519 | 0.37211 | 0.39288 | 0.41018 | 0.42403 | 0.43095 | 40.92 | 26.99 | 7.21 | 2.88 | 1.31 | 0.53 | 0 | 0 | 0 | Dynalene PG Data Sheet
Dynalene® PG - 60 Vol% | Dynalene | Propylene glycol with corrosion inhibitors | -28.8889 | 121.1111 |  |  |  |  | -4.271 | 936.2342 | -150.3614 | -0.65217 | 1056.3829 | 0.00029899 | 0.31243 | 0.00441 | 3.2529 | [5 empty] | -34.4444 | -28.8889 | -1.1111 | 26.6667 | 60 | 104.4444 | 1074.0377 | 1072.1155 | 1060.7424 | 1045.3647 | 1021.8176 | 981.6112 | 3.1024 | 3.1234 | 3.249 | 3.3704 | 3.5169 | 3.7137 | 0.29596 | 0.30115 | 0.31672 | 0.32711 | 0.3349 | 0.33663 | 497.57 | 298.75 | 33.68 | 7.34 | 2.22 | 0.86 | 0 | 0 | 0 | Dynalene PG Data Sheet
Dynalene® PG - 80 Vol% | Dynalene | Propylene glycol with corrosion inhibitors | -28.8889 | 121.1111 |  |  |  |  | -4.6103 | 1143.8308 | -143.2188 | -0.7901 | 1069.0127 | 2.6401e-06 | 0.25754 | 0.0050518 | 2.7634 | [5 empty] | -34.4444 | -28.8889 | -1.1111 | 26.6667 | 60 | 104.4444 | 1095.3423 | 1091.3377 | 1070.5137 | 1049.0489 | 1022.4583 | 985.2955 | 2.5749 | 2.6084 | 2.7633 | 2.914 | 3.0982 | 3.2615 | 0.25442 | 0.25615 | 0.25961 | 0.26134 | 0.25961 | 0.25442 | 1363.75 | 820.58 | 80.66 | 14.79 | 3.82 | 1.31 | 0 | 0 | 0 | Dynalene PG Data Sheet
Dynalene® SF | Dynalene | Synthetic alkylated aromatics | 0 | 315 |  |  |  |  | -3.4851 | 1205.7573 | -123.2289 | -0.67317 | 890.3946 | -7.9806e-05 | 0.13641 | 0.0036539 | 1.8939 | 180 | 330 |  |  |  | 0 | 20 | 90 | 160 | 240 | 315 | 890 | 877 | 830 | 783 | 729 | 678 | 1.894 | 1.967 | 2.223 | 2.478 | 2.771 | 3.045 | 0.1361 | 0.1347 | 0.1295 | 0.124 | 0.1174 | 0.1109 | 160 | 37 | 4.1 | 1.5 | 0.69 | 0.41 | 0 | 0 | 0 | Dynalene SF Data Sheet
Ethyl Alcohol | 0 | pure component | 0 | 0 |  | 8.2423 | 1664.5212 | 232.3398 | -11.7068 | 8152.45 | 393.0424 | -0.859 | 806.45 | 0 | 0.18173 | 0.015025 | 2.055 | 13 | 78.4 |  | 46.07 | 842 | -10 | 0 | 10 | 20 | 30 | 40 | 815.04 | 806.45 | 797.86 | 789.27 | 780.68 | 772.09 | 1.9134 | 2.0515 | 2.1981 | 2.353 | 2.5037 | 2.6628 | 0.18173 | 0.18173 | 0.18173 | 0.18173 | 0.18173 | 0.18173 | 2.07 | 1.7 | 1.4 | 1.19 | 0.98 | 0.85 | 11.97 | 44.25 | 135 | Perry's, 6th Ed
Glycerol | 0 | pure component | 0 | 0 |  |  |  |  | -38.7259 | 37120.5808 | 525.3966 | -2.6132 | 1293.347 | 0 | 0.28384 | 0.0051677 | 2.2869 | 160 | 290 |  | 92.1 | 663 | 60 | 80 | 100 | 120 | 140 | 160 | 1136.555 | 1084.291 | 1032.027 | 979.763 | 927.499 | 875.235 | 2.5958 | 2.7005 | 2.8052 | 2.9056 | 3.0145 | 3.1108 | 0.28384 | 0.28384 | 0.28384 | 0.28384 | 0.28384 | 0.28384 | 92 | 34 | 13.5 | 5.4 | 2.4 | 1 | 0 | 0 | 0 | Perry's, 6th Ed
Hexane | 0 | pure component | 0 | 0 |  | 6.7033 | 1088.1131 | 215.7521 | -6.6653 | 3106.1265 | 275.2299 | -0.92017 | 678.1547 | -0.00036794 | 0.13035 | 0.0030889 | 2.1691 | -21.6667 | 68.7778 |  | 86.177 | 334.944 | -20 | 0 | 20 | 40 | 60 | 80 | 695.29 | 678.3378 | 660.7597 | 642.4579 | 623.3074 | 603.1444 | 2.1197 | 2.1681 | 2.2211 | 2.281 | 2.3501 | 2.4309 | 0.13739 | 0.13041 | 0.12324 | 0.11588 | 0.10833 | 0.1006 | 0.46462 | 0.36746 | 0.30003 | 0.25002 | 0.21082 | 0.17866 | 45.7017 | 281.0088 | 1057.165 | Yaw's Handbook, 2003
Marlotherm® FP | Sasol | Isoparaffinic chemical structure, clear liquid, bland odor | 60 | 300 |  | 0.71076 | 588.6311 | -607.7826 | -4.4628 | 1669.133 | -79.9073 | -0.65682 | 861.6443 | -6.0901e-05 | 0.1344 | 0.0037649 | 1.837 | 216 | 340 |  |  |  | 20 | 60 | 100 | 160 | 220 | 300 | 847 | 822 | 797 | 758 | 718 | 663 | 1.95 | 2.07 | 2.19 | 2.4 | 2.64 | 3.01 | 0.133 | 0.131 | 0.128 | 0.125 | 0.121 | 0.116 | 40.1 | 8.4 | 3.3 | 1.3 | 0.71 | 0.34 | 61 | 106 | 420 | Marlotherm FP Technical Data Sheet, Rev: 11-May-2004
Marlotherm® LH | Sasol | Skynthetic, organic, heat transfer medium | 0 | 280 |  |  |  |  | -2.765 | 699.2382 | -125.2071 | -0.80729 | 1013.83 | -0.00011522 | 0.13375 | 0.0033478 | 1.5475 | 130 | 278 |  |  |  | 0 | 40 | 100 | 160 | 220 | 300 | 1010 | 980 | 936 | 890 | 839 | 766 | 1.55 | 1.68 | 1.88 | 2.08 | 2.29 | 2.55 | 0.134 | 0.129 | 0.122 | 0.115 | 0.109 | 0.099 | 8.3 | 2.6 | 1.1 | 0.61 | 0.43 | 0.3 | 0 | 0 | 0 | Marlotherm LH Product Information, Rev: 09.04
Marlotherm® N | Sasol | Skynthetic, organic, heat transfer medium, ideal 150 to 300 deg C range | 20 | 300 |  |  |  |  | -4.3701 | 1719.2336 | -67.8658 | -0.67167 | 890.128 | -8.1322e-05 | 0.13678 | 0.0036653 | 1.8924 | 180 | 330 |  |  |  | 0 | 40 | 100 | 160 | 220 | 300 | 890 | 863 | 823 | 783 | 743 | 688 | 1.89 | 2.04 | 2.26 | 2.48 | 2.7 | 2.99 | 0.136 | 0.134 | 0.129 | 0.124 | 0.119 | 0.112 | 123 | 14 | 3 | 1.4 | 0.73 | 0.38 | 0 | 0 | 0 | Marlotherm N Product Information, Rev: 01.06.2007
Marlotherm® SH | Sasol | Skynthetic, organic, heat transfer medium | 20 | 340 |  |  |  |  | -3.1438 | 1006.8454 | -143.8527 | -0.71438 | 1058.298 | -0.0001309 | 0.13306 | 0.0037062 | 1.4768 | 200 | 385 |  |  |  | 0 | 40 | 100 | 160 | 220 | 300 | 1058 | 1030 | 987 | 944 | 901 | 844 | 1.48 | 1.62 | 1.85 | 2.07 | 2.29 | 2.59 | 0.133 | 0.128 | 0.12 | 0.112 | 0.104 | 0.094 | 321 | 16.5 | 3.1 | 1.4 | 0.77 | 0.45 | 0 | 0 | 0 | Marlotherm SH Product Information, Rev: 09/04
Methyl Alcohol | 0 | pure component | 0 | 0 |  | 7.9749 | 1515.293 | 232.9925 | -3.7419 | 790.396 | -48.5242 | -0.925 | 810.1833 | 0 | 0.21461 | 0.0043184 | 2.4131 | 12 | 64.7 |  | 32.04 | 1100 | -10 | 0 | 10 | 20 | 30 | 40 | 819.4333 | 810.1833 | 800.9333 | 791.6833 | 782.4333 | 773.1833 | 2.3655 | 2.42 | 2.4618 | 2.487 | 2.5456 | 2.5874 | 0.21461 | 0.21461 | 0.21461 | 0.21461 | 0.21461 | 0.21461 | 0.92 | 0.8 | 0.69 | 0.6 | 0.52 | 0.47 | 29.6 | 96.7 | 265.6 | Perry's, 6th Ed
MultiTherm® 503 | MultiTherm | Paraffinic hydrocarbon | -5 | 260 |  |  |  |  | -3.7152 | 1037.3867 | -112.624 | -0.65445 | 806.9452 | -6.1781e-05 | 0.14259 | 0.0038106 | 2.0241 | 154 | 338 |  |  |  | -20 | 0 | 60 | 120 | 180 | 260 | 820 | 807 | 768 | 728 | 689 | 637 | 1.948 | 2.024 | 2.253 | 2.481 | 2.71 | 3.015 | 0.1438 | 0.1426 | 0.1389 | 0.1352 | 0.1315 | 0.1265 | 45 | 15.6 | 2.49 | 0.983 | 0.529 | 0.287 | 0 | 0 | 0 | MultiTherm 503 7/04 Data Sheet
MultiTherm® FF-1 | MultiTherm | Flushing Fluid | -18 | 260 |  | 7.5157 | 3644.821 | 270.4466 | -3.3435 | 955.1227 | -161.0656 | -0.64814 | 921.0921 | -7.2014e-05 | 0.12905 | 0.0043361 | 1.7237 | 160 | 271 |  |  |  | -18 | 38 | 93 | 149 | 204 | 260 | 932 | 897 | 861 | 825 | 789 | 752 | 1.63 | 1.88 | 2.14 | 2.39 | 2.64 | 2.81 | 0.1303 | 0.1264 | 0.1223 | 0.1184 | 0.1142 | 0.1104 | 1412 | 20.5 | 3.53 | 1.37 | 0.73 | 0.46 | 5e-05 | 0.067 | 4.41 | MultiTherm FF-1 7/04 Data Sheet
MultiTherm® IG-1 | MultiTherm | White mineral oil | -20 | 288 |  |  |  |  | -2.8904 | 907.4314 | -174.3556 | -0.52528 | 871.6567 | -7.5882e-05 | 0.13996 | 0.0036415 | 1.8132 | 228 | 374 |  |  |  | -20 | -10 | 40 | 120 | 220 | 320 | 884 | 879 | 850 | 805 | 752 | 708 | 1.742 | 1.777 | 1.959 | 2.248 | 2.612 | 2.981 | 0.1416 | 0.1412 | 0.1359 | 0.1312 | 0.1234 | 0.1156 | 2679 | 1524 | 33.94 | 3.515 | 1.002 | 0.485 | 0 | 0 | 0 | MultiTherm IG-1 Web Page (2010)
MultiTherm® IG-4 | MultiTherm | White mineral oil | -10 | 316 |  |  |  |  | -3.2384 | 1030.8061 | -162.5832 | -0.71021 | 877.6741 | -7.3178e-05 | 0.1356 | 0.0045476 | 1.8635 | 227 | 411 | Mineral Oil |  |  | -10 | 0 | 60 | 140 | 200 | 300 | 882 | 875 | 837 | 783 | 740 | 659 | 1.818 | 1.864 | 2.136 | 2.5 | 2.773 | 3.228 | 0.1363 | 0.1356 | 0.1312 | 0.1254 | 0.121 | 0.1136 | 1121 | 439 | 15.6 | 2.4 | 1.13 | 0.483 | 0 | 0 | 0 | MultiTherm IG-4 Web Page (2010)
MultiTherm® OG-1 | MultiTherm | Hydrocracked mineral oil with oxidation inhibitor/stabilizer | 0 | 290 |  |  |  |  | -2.6684 | 863.5164 | -172.9332 | -0.53598 | 871.6843 | -3.652e-05 | 0.13951 | 0.0035631 | 1.7943 | 235 | 373 | Mineral Oil |  |  | -10 | 0 | 60 | 120 | 200 | 300 | 879 | 872 | 839 | 805 | 763 | 713 | 1.777 | 1.813 | 2.01 | 2.177 | 2.47 | 2.906 | 0.1412 | 0.1388 | 0.1365 | 0.1353 | 0.1319 | 0.1289 | 1524 | 383 | 15.6 | 3.5 | 1.3 | 0.6 | 0 | 0 | 0 | MultiTherm OG-1 7/04 Data Sheet
MultiTherm® PG-1 | MultiTherm | White mineral oil, food grade | -20 | 316 |  |  |  |  | -3.1587 | 876.1354 | -167.0308 | -0.42033 | 881.6659 | -7.2308e-05 | 0.13443 | 0.0036329 | 1.8054 | 171 | 349 | Mineral Oil |  |  | -30 | -20 | 40 | 100 | 180 | 320 | 894 | 890 | 865 | 840 | 806 | 747 | 1.696 | 1.733 | 1.951 | 2.169 | 2.459 | 2.968 | 0.1366 | 0.1359 | 0.1315 | 0.1272 | 0.1214 | 0.1113 | 4113 | 1113 | 16 | 2.98 | 0.975 | 0.332 | 0 | 0 | 0 | MultiTherm PG-1 7/04 Data Sheet
MultiTherm® ULT-170 | MultiTherm | Hydrocarbon blend | -112 | 38 |  |  |  |  | -1.6962 | 283.955 | -121.5485 | -0.7704 | 860.46 | -0.0002 | 0.1377 | 0.0035024 | 1.725 | 53 | 176 |  |  |  | -125 | -100 | -75 | -50 | 0 | 50 | 956.76 | 937.5 | 918.24 | 898.98 | 860.46 | 821.94 | 1.287 | 1.375 | 1.462 | 1.55 | 1.725 | 1.9 | 0.1627 | 0.1577 | 0.1527 | 0.1477 | 0.1377 | 0.1277 | 0 | 45 | 8 | 3 | 1.2 | 0.75 | 0 | 0 | 0 | MultiTherm ULT-170 7/04 Data Sheet
MultiTherm® WB+14 | MultiTherm | Water based, no flash point, for low temperature performance | -10 | 121 |  |  |  |  | -27.5351 | 49896.876 | 1485.7617 | -0.47946 | 1200.6784 | 0.001 | 0.506 | 0.0025297 | 3.2805 | [5 empty] | -10 | 0 | 25 | 50 | 75 | 100 | 1205 | 1200 | 1190 | 1177 | 1165 | 1152 | 3.25 | 3.28 | 3.35 | 3.41 | 3.47 | 3.53 | 0.496 | 0.506 | 0.531 | 0.556 | 0.581 | 0.606 | 3 | 2.3 | 1.5 | 1.05 | 0.7 | 0.5 | 0 | 0 | 0 | MultiThermWB 7/04 Data Sheet
MultiTherm® WB-22 | MultiTherm | Water based, no flash point, for low temperature performance | -30 | 121 |  |  |  |  | -1.5498 | 217.121 | -191.1672 | -0.49829 | 1285.3524 | 0.001 | 0.499 | 0.0022286 | 3.0414 | [5 empty] | -25 | 0 | 25 | 50 | 75 | 100 | 1298 | 1285 | 1273 | 1260 | 1249 | 1235 | 3 | 3.03 | 3.09 | 3.15 | 3.21 | 3.27 | 0.474 | 0.499 | 0.524 | 0.549 | 0.574 | 0.599 | 10 | 3 | 1.9 | 1.1 | 0.9 | 0.7 | 0 | 0 | 0 | MultiThermWB 7/04 Data Sheet
MultiTherm® WB-40 | MultiTherm | Water based, no flash point, for low temperature performance | -40 | 121 |  |  |  |  | -1.1973 | 266.8391 | -166.7157 | -0.57375 | 1325.5187 | 0.0010794 | 0.48638 | 0.002195 | 2.8914 | [5 empty] | -40 | -25 | 0 | 25 | 50 | 100 | 1350 | 1340 | 1325 | 1310 | 1295 | 1270 | 2.8 | 2.84 | 2.89 | 2.95 | 3 | 3.11 | 0.437 | 0.463 | 0.489 | 0.515 | 0.541 | 0.592 | 15 | 8 | 4 | 2.3 | 1.7 | 1.1 | 0 | 0 | 0 | MultiThermWB 7/04 Data Sheet
MultiTherm® WB-5 | MultiTherm | Water based, no flash point, for low temperature performance | -20 | 121 |  |  |  |  | -1.0665 | 193.5886 | -191.6335 | -0.52806 | 1249.5758 | 0.001 | 0.505 | 0.0022677 | 3.1814 | [5 empty] | -20 | 0 | 25 | 50 | 75 | 100 | 1258 | 1249 | 1240 | 1224 | 1210 | 1195 | 3.13 | 3.19 | 3.24 | 3.29 | 3.35 | 3.41 | 0.485 | 0.505 | 0.53 | 0.555 | 0.58 | 0.605 | 5 | 3.7 | 2.2 | 1.5 | 1.2 | 1 | 0 | 0 | 0 | MultiThermWB 7/04 Data Sheet
MultiTherm® WB-58 | MultiTherm | Water based, no flash point, for low temperature performance | -50 | 121 |  |  |  |  | -2.0195 | 517.6447 | -128.3839 | -0.6 | 1365 | 0.0010326 | 0.48446 | 0.00208 | 2.662 | [5 empty] | -50 | -25 | 0 | 25 | 50 | 100 | 1395 | 1380 | 1365 | 1350 | 1335 | 1305 | 2.56 | 2.61 | 2.66 | 2.71 | 2.77 | 2.87 | 0.433 | 0.459 | 0.484 | 0.51 | 0.536 | 0.588 | 40 | 10 | 4.5 | 2.8 | 2 | 1.1 | 0 | 0 | 0 | MultiThermWB 7/04 Data Sheet
Octane | 0 | pure component | 0 | 0 |  | 7.0958 | 1455.3137 | 219.7033 | -6.8339 | 3563.9671 | 276.8476 | -0.83693 | 718.2331 | -0.00031032 | 0.13642 | 0.0028639 | 2.1661 | 13.3333 | 125.6667 |  | 114.231 | 302.38 | -20 | 20 | 60 | 100 | 120 | 140 | 732.5191 | 702.5186 | 670.5874 | 636.161 | 617.7531 | 598.3474 | 2.1285 | 2.2182 | 2.3152 | 2.4352 | 2.5086 | 2.5937 | 0.14198 | 0.13053 | 0.11845 | 0.10573 | 0.099123 | 0.092362 | 1.0076 | 0.55915 | 0.36575 | 0.25901 | 0.22073 | 0.18848 | 10.5791 | 349.6937 | 1121.7379 | Yaw's Handbook, 2003
Paratherm CR™ | Paratherm | Synthetic hydrocarbon blend | -95.5556 | 218.3333 |  | 5.922 | 1219.838 | 210.0557 | -2.7848 | 568.8911 | -70.8208 | -1.0082 | 848.287 | -7.6521e-05 | 0.14164 | 0.0037174 | 1.8463 | 40 | 180 |  |  |  | -101.1111 | -73.3333 | -17.7778 | 37.7778 | 93.3333 | 204.4444 | 950.215 | 922.1827 | 866.2783 | 810.2137 | 754.1491 | 642.1801 | 1.4704 | 1.5738 | 1.7802 | 1.9866 | 2.1935 | 2.6063 | 0.14936 | 0.14729 | 0.14279 | 0.1388 | 0.13482 | 0.12582 | 36 | 5.08 | 1.58 | 0.66 | 0.42 | 0.25 | 0.001 | 10 | 953 | Engineering Bulleting CR 809
Paratherm GLT™ | Paratherm | Alkylated aromatic for closed loop liquid phase heating | 35 | 301.6667 |  | 8.3579 | 3690.1919 | 318.4912 | -3.7743 | 1137.4461 | -140.2596 | -0.69565 | 892.8101 | -0.0001413 | 0.13286 | 0.0032052 | 1.874 | 182 | 500 |  |  |  | -6.6667 | 37.7778 | 93.3333 | 148.8889 | 226.6667 | 315.5556 | 897.0338 | 864.9968 | 832.9599 | 784.9045 | 736.8492 | 672.7753 | 1.8422 | 2.0097 | 2.1771 | 2.3446 | 2.5958 | 2.8889 | 0.13327 | 0.12807 | 0.11942 | 0.1125 | 0.10038 | 0.088267 | 254 | 18 | 3.2 | 1.3 | 0.58 | 0.29 | 0.01 | 2.9 | 345 | Engineering Bulleting GLT 309
Paratherm HE™ | Paratherm | Hydrotreated heavy paraffinic distillate - mineral oil | 52.7778 | 310 |  | -4.5986 | 1009.0387 | -476.955 | -3.1959 | 1055.9068 | -156.1076 | -0.64128 | 875.9411 | -7.5445e-05 | 0.13425 | 0.0036466 | 1.8114 | 221 | 500 | Mineral Oil |  |  | 15.5556 | 37.7778 | 93.3333 | 148.8889 | 226.6667 | 315.5556 | 865.9579 | 851.7015 | 816.1405 | 780.4194 | 730.602 | 673.5762 | 1.8682 | 1.9494 | 2.1516 | 2.3542 | 2.6381 | 2.9622 | 0.13309 | 0.13136 | 0.12721 | 0.12306 | 0.11717 | 0.11042 | 126 | 37.5 | 6.01 | 2.17 | 0.94 | 0.47 | 0.005 | 0.03 | 45 | Engineering Bulleting HE 809
Paratherm HR™ | Paratherm | Alkylated aromatic, for closed loop heating | 25 | 357.2222 |  | 19.1764 | 25786.0495 | 1240.2533 | -3.7334 | 1159.4196 | -121.8292 | -0.76651 | 971.0799 | -9.9485e-05 | 0.12235 | 0.0022206 | 1.8994 | 160 | 335 |  |  |  | 10 | 37.7778 | 121.1111 | 176.6667 | 260 | 371.1111 | 961.1076 | 945.0891 | 881.0153 | 832.9599 | 768.8861 | 688.7938 | 1.9259 | 1.9678 | 2.1771 | 2.3027 | 2.4702 | 2.7214 | 0.11769 | 0.11769 | 0.1125 | 0.10904 | 0.098652 | 0.081345 | 50 | 11 | 1.5 | 0.82 | 0.42 | 0.22 | 0.1 | 9.5 | 1492 | Engineering Bulleting HR 309
Paratherm LR™ | Paratherm | Paraffinic hydrocarbon, for closed loop heating and cooling | -49.4444 | 248.8889 |  | 7.4989 | 2118.7409 | 241.8051 | -4.0513 | 992.5832 | -80.5601 | -0.73775 | 777.6371 | -7.7416e-05 | 0.15264 | 0.003874 | 1.9248 | 54 | 200 |  |  |  | -73.3333 | -40 | 15.5556 | 93.3333 | 148.8889 | 232.2222 | 831.8386 | 807.01 | 766.1629 | 708.8169 | 667.8096 | 606.2987 | 1.6408 | 1.7698 | 1.985 | 2.2864 | 2.5016 | 2.8244 | 0.15836 | 0.15594 | 0.15092 | 0.14573 | 0.14105 | 0.13465 | 138.19 | 11.63 | 1.83 | 0.56 | 0.32 | 0.18 | 0.001 | 15.03 | 1069.76 | Engineering Bulleting LR 809
Paratherm MG™ | Paratherm | Linear alkene, food grade | 2.2222 | 304.4444 |  | 15.5673 | 14491.9443 | 814.9375 | -2.9951 | 757.8406 | -148.6413 | -0.56305 | 809.5163 | -8.5355e-05 | 0.13506 | 0.0020286 | 2.3338 | 149 | 400 |  |  |  | -17.7778 | 10 | 65.5556 | 148.8889 | 232.2222 | 315.5556 | 840.9692 | 810.5341 | 756.0713 | 700.0067 | 669.5716 | 655.155 | 2.3027 | 2.3446 | 2.4702 | 2.6377 | 2.8052 | 2.9726 | 0.13327 | 0.13327 | 0.13154 | 0.12634 | 0.11769 | 0.10384 | 60 | 14 | 2.9 | 0.8 | 0.39 | 0.28 | 0.01 | 3.4 | 560 | Engineering Bulleting MG 709
Paratherm MR™ | Paratherm | Linear alkene, fully saturated | -3.8889 | 248.8889 |  |  |  |  | -2.7978 | 620.4392 | -163.7357 | -0.73934 | 816.41 | -5.5092e-05 | 0.13418 | 0.0019198 | 2.3386 | 135 | 500 |  |  |  | -17.7778 | 10 | 37.7778 | 93.3333 | 148.8889 | 204.4444 | 840.9692 | 810.5341 | 781.7008 | 735.2473 | 700.0067 | 677.5809 | 2.3027 | 2.3446 | 2.4283 | 2.5121 | 2.6377 | 2.7214 | 0.13327 | 0.13327 | 0.13327 | 0.13154 | 0.12634 | 0.12115 | 40 | 11 | 4.3 | 1.3 | 0.66 | 0.44 | 0 | 0 | 0 | Engineering Bulleting MR 909
Paratherm NF™ | Paratherm | Hydrotreated mineral oil, food grade | 35.5556 | 332.2222 |  | 3.5182 | 568.508 | 65.2458 | -11.0429 | 7675.2836 | 244.6278 | -0.66273 | 897.7319 | -5.0915e-05 | 0.10576 | 0.0052866 | 1.7181 | 157 | 500 | Mineral Oil |  |  | 10 | 37.7778 | 93.3333 | 148.8889 | 232.2222 | 315.5556 | 890.6264 | 873.0061 | 836.1636 | 799.3212 | 743.2565 | 688.7938 | 1.7585 | 1.9259 | 2.219 | 2.5121 | 2.9308 | 3.3913 | 0.10557 | 0.10384 | 0.10038 | 0.098652 | 0.09346 | 0.089998 | 83 | 16 | 3.2 | 1.6 | 0.53 | 0.16 | 0.01 | 7.3 | 106 | Engineering Bulleting NF 809
Pentane | 0 | pure component | 0 | 0 |  | 6.815 | 1036.9219 | 227.6363 | -4.9579 | 1823.4144 | 215.8152 | -0.9576 | 644.4961 | -0.00024132 | 0.15372 | 0.0031607 | 2.1967 | -49.4444 | 36.0556 |  | 72.15 | 357.5062 | -50 | -30 | -10 | 10 | 30 | 50 | 691.0265 | 673.4161 | 655.1448 | 636.1055 | 616.1598 | 595.124 | 2.0522 | 2.1007 | 2.1543 | 2.2155 | 2.2868 | 2.3708 | 0.1652 | 0.16107 | 0.15659 | 0.15177 | 0.14659 | 0.14107 | 0.46466 | 0.37344 | 0.31436 | 0.27158 | 0.23719 | 0.20707 | 37.0155 | 282.8251 | 1202.762 | Yaw's Handbook, 2003
Petro-Therm™ | Petro-Canada | Mixture of severely hydrotreated and hydrocracked petroleum | 25 | 315 |  |  |  |  | -2.602 | 745.2366 | -188.0981 | -0.63256 | 878.7054 | 0 | 0 | 0.0032743 | 1.8424 | 225 | 376 |  |  |  | 15 | 38 | 260 | 260 | 316 | 316 | 869 | 855 | 714 | 714 | 679 | 679 | 1.89 | 1.97 | 2.69 | 2.69 | 2.88 | 2.88 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9 | 31.635 | 0.6426 | 0.6426 | 0.4753 | 0.4753 | 0 | 0 | 0 | 0
Propyl Alcohol, i- | 0 | pure component | 0 | 0 |  | 8.0709 | 1562.6772 | 218.6912 | -13.5289 | 8140.3343 | 275.494 | -0.81795 | 801.5741 | -9.2464e-05 | 0.16129 | 0.01273 | 2.4286 | 12 | 82.5 |  | 60.1 | 663 | -10 | 0 | 20 | 40 | 60 | 80 | 809.7536 | 801.5741 | 785.2152 | 768.8563 | 752.4973 | 736.1384 | 2.3027 | 2.4283 | 2.6837 | 2.9391 | 3.182 | 3.4541 | 0.16269 | 0.16096 | 0.15923 | 0.1575 | 0.15577 | 0.15404 | 4.8 | 3.7 | 2.25 | 1.35 | 0.87 | 0.56 | 8.42 | 107.2 | 690.48 | Perry's, 6th Ed
Propyl Alcohol, n- | 0 | pure component | 0 | 0 |  | 8.0603 | 1608.4238 | 213.4908 | -9.3739 | 4628.1372 | 160.1067 | -0.78667 | 819.4333 | 0.00018493 | 0.15683 | 0.0097799 | 2.2317 | 15 | 97.8 |  | 60.1 | 695 | -10 | 0 | 20 | 40 | 60 | 80 | 827.3 | 819.4333 | 803.7 | 787.9667 | 772.2333 | 756.5 | 2.1353 | 2.2274 | 2.4283 | 2.6293 | 2.8135 | 3.0145 | 0.15404 | 0.1575 | 0.16096 | 0.16442 | 0.16788 | 0.17134 | 4.7 | 3.7 | 2.35 | 1.5 | 1 | 0.7 | 3.36 | 51.9 | 380.14 | Perry's, 6th Ed
PURITY™ FG | Petro-Canada | Pure base oil, food grade, with additives | 4 | 326 |  | -3.5924 | 600.9665 | -417.3932 | -3.0244 | 966.3913 | -162.6162 | -0.67729 | 864.7274 | -5.6371e-05 | 0.13907 | 0.0033925 | 1.8061 | 209 | 382 |  |  |  | 15 | 40 | 40 | 100 | 260 | 316 | 853.7839 | 837.7655 | 837.7655 | 797.7193 | 688.7938 | 650.3495 | 1.8673 | 1.9385 | 1.9385 | 2.1395 | 2.6879 | 2.8805 | 0.13846 | 0.13673 | 0.13673 | 0.13327 | 0.12461 | 0.12115 | 0 | 29.8245 | 0 | 4.7863 | 0 | 0.46825 | 0.01 | 0.02 | 216.1088 | Petro-Canada, TechData Sheet IM-7877E (04.03)
SYLTHERM™ 800 | Dow Chemical | Silicone fluid - dimethyl polysiloxane | -40 | 400 |  | 5.9015 | 992.7442 | 125.6404 | -6.1614 | 4125.9096 | 190.8927 | -0.98672 | 957.6492 | -0.00018818 | 0.13878 | 0.0017077 | 1.5742 | 160 | 330 |  |  |  | -40 | 0 | 120 | 240 | 320 | 400 | 990.61 | 953.16 | 846.35 | 734.35 | 648.24 | 547 | 1.506 | 1.574 | 1.779 | 1.984 | 2.121 | 2.257 | 0.1463 | 0.1388 | 0.1162 | 0.0936 | 0.0786 | 0.0635 | 51.05 | 15.33 | 2.36 | 0.74 | 0.41 | 0.25 | 0.01 | 1536 | 10300 | Dow, SYLTHERM™ 800 Product Information Sheet, Nov 2001
SYLTHERM™ HF | Dow Chemical | Silicone fluid - dimethyl polysiloxane | -73 | 260 |  | 16.1065 | 14388.5762 | 864.6651 | -4.1346 | 1402.5367 | 2.0823 | -1.011 | 891.9793 | -0.00024799 | 0.11196 | 0.0024635 | 1.6326 | 63 | 210 |  |  |  | -73 | -70 | -20 | 80 | 180 | 260 | 965.78 | 962.75 | 912.2 | 811.1 | 710 | 629.12 | 1.453 | 1.46 | 1.583 | 1.83 | 2.076 | 2.273 | 0.1301 | 0.1293 | 0.1169 | 0.0921 | 0.0673 | 0.0475 | 16.46 | 14.87 | 3.88 | 0.83 | 0.35 | 0.22 | 0.01 | 7.5 | 2055 | Dow, SYLTHERM™ HF Product Information Sheet, Nov 2001
SYLTHERM™ XLT | Dow Chemical | Silicone fluid - dimethyl polysiloxane | -100 | 260 |  | 6.3788 | 1168.299 | 159.4352 | -3.6936 | 958.0563 | -54.5892 | -1.0272 | 875.815 | -0.00023429 | 0.11355 | 0.0021 | 1.73 | 47 | 175 |  |  |  | -100 | -20 | 60 | 140 | 220 | 280 | 978.5 | 896.4 | 814.2 | 732 | 649.8 | 588.2 | 1.52 | 1.688 | 1.856 | 2.024 | 2.192 | 2.318 | 0.1341 | 0.1192 | 0.1019 | 0.0827 | 0.062 | 0.0455 | 78.6 | 3.1 | 0.8 | 0.36 | 0.22 | 0.17 | 0.01 | 300 | 5250 | Dow, SYLTHERM™ XLT Product Information Sheet, Dec 2003
Thermalane® 600 | Coastal Chemical | Premium heat transfer fluid, non-toxic, environmentally friendly | 65.5556 | 315.5556 |  | 461.7899 | 15857160.5917 | 34222.7731 | -3.0205 | 847.1828 | -177.2802 | -0.70765 | 922.4705 | -0.00020072 | 0.17002 | 0.0039511 | 1.6919 | 176.6667 | 269.4444 |  |  |  | 37.7778 | 93.3333 | 148.8889 | 204.4444 | 260 | 315.5556 | 892.2282 | 856.9876 | 820.1452 | 780.099 | 740.0529 | 695.2012 | 1.8422 | 2.0515 | 2.2818 | 2.5121 | 2.7214 | 2.9308 | 0.16096 | 0.15144 | 0.14192 | 0.12981 | 0.11769 | 0.10557 | 29.845 | 4.2935 | 1.5419 | 0.8191 | 0.53284 | 0.38236 | 0.5 | 15.5 | 470 | Thermalane 600 Data Sheet, 2010
Thermalane® 800 | Coastal Chemical | Premium heat transfer fluid, non-toxic, environmentally friendly | 65.5556 | 315.5556 |  | 44.2931 | 139253.2253 | 2981.1591 | -2.886 | 889.1566 | -145.1724 | -0.65905 | 826.583 | -0.00010503 | 0.15298 | 0.0030145 | 2.1889 | 229.4444 | 376.6667 |  |  |  | 37.7778 | 93.3333 | 148.8889 | 204.4444 | 260 | 315.5556 | 800.923 | 765.6824 | 728.8399 | 691.9975 | 655.155 | 618.3126 | 2.3027 | 2.4702 | 2.6377 | 2.8052 | 2.9726 | 3.1401 | 0.14884 | 0.14365 | 0.13673 | 0.13154 | 0.12634 | 0.11942 | 13.2953 | 3.101 | 1.3921 | 0.80964 | 0.56343 | 0.41427 | 0.1 | 3.8 | 113 | Thermalane 800 Data Sheet, 2010
Therminol™ 55 | Solutia | Alkyl aromatic derivatives | -25 | 290 |  | 8.3175 | 3488.5436 | 290.5608 | -3.3187 | 932.6134 | -160.7487 | -0.69514 | 885.8071 | -0.00011657 | 0.13073 | 0.0035423 | 1.8351 | 177 | 340 | Synthetic Hydrocarbon |  |  | -25 | 25 | 75 | 125 | 175 | 275 | 901 | 868 | 835 | 801 | 766 | 692 | 1.744 | 1.924 | 2.102 | 2.28 | 2.456 | 2.807 | 0.1336 | 0.1278 | 0.122 | 0.1162 | 0.1104 | 0.0986 | 1250 | 32.1 | 5.14 | 1.84 | 0.963 | 0.402 | 0.00183 | 0.837 | 141 | Therminol Reference Disk, Version 5.0
Therminol™ 59 | Solutia | Mixture of diphenyl alkanes | -45 | 315 |  | 7.0979 | 2163.0937 | 223.74 | -3.7408 | 1121.9099 | -96.0447 | -0.77286 | 989.8786 | -0.00010143 | 0.12321 | 0.0033343 | 1.6141 | 138 | 289 | Alkyl Substituted Aromatic |  |  | -45 | 15 | 75 | 135 | 195 | 315 | 1020 | 978 | 934 | 890 | 843 | 741 | 1.472 | 1.665 | 1.86 | 2.057 | 2.257 | 2.674 | 0.1253 | 0.1217 | 0.1171 | 0.1115 | 0.1049 | 0.0888 | 991 | 8.16 | 1.92 | 0.864 | 0.496 | 0.232 | 0.0109 | 11.7 | 1210 | Therminol Reference Disk, Version 5.0
Therminol™ 62 | Solutia | Mixture of di- and tri-isopropyl biphenyl | -20 | 325 |  | 8.0257 | 3088.7592 | 267.4716 | -4.4801 | 1412.1785 | -112.8276 | -0.76952 | 970.7048 | -9.8667e-05 | 0.12509 | 0.0022167 | 1.902 | 149 | 310 |  |  |  | -20 | 40 | 100 | 160 | 220 | 280 | 982 | 940 | 897 | 852 | 803 | 750 | 1.832 | 1.997 | 2.144 | 2.276 | 2.393 | 2.499 | 0.1263 | 0.1212 | 0.1158 | 0.1101 | 0.1037 | 0.0965 | 1180 | 10.1 | 2.26 | 0.931 | 0.48 | 0.28 | 0.00955 | 6.31 | 242 | Therminol Reference Disk, Version 5.0
Therminol™ 66 | Solutia | Hydrogenated terphenyl and polyphenyls | 0 | 345 |  | 8.4917 | 3904.1731 | 337.0986 | -2.9608 | 798.1315 | -188.7882 | -0.70095 | 1022.8095 | -7.9095e-05 | 0.12015 | 0.0035776 | 1.4859 | 170 | 359 | Modified Terphenyl |  |  | 0 | 60 | 120 | 180 | 240 | 300 | 1020 | 981 | 941 | 899 | 856 | 809 | 1.495 | 1.699 | 1.908 | 2.122 | 2.342 | 2.569 | 0.1183 | 0.1158 | 0.1121 | 0.1074 | 0.1015 | 0.0946 | 1320 | 11.5 | 2.42 | 1.06 | 0.611 | 0.413 | 0.0457 | 8.74 | 231 | Therminol Reference Disk, Version 5.0
Therminol™ 72 | Solutia | Mixture of diphenyl ether, terphenyl, biphenyl, and phenanthrene | -10 | 380 |  | 73.3829 | 710633.5074 | 9808.2917 | -4.5393 | 1495.1391 | -83.8053 | -0.9098 | 1097.9497 | -0.00012143 | 0.14199 | 0.002709 | 1.4982 | 132 | 271 |  |  |  | -10 | 60 | 130 | 200 | 270 | 340 | 1110 | 1040 | 979 | 916 | 853 | 789 | 1.471 | 1.661 | 1.85 | 2.04 | 2.23 | 2.419 | 0.1432 | 0.1347 | 0.1262 | 0.1177 | 0.1092 | 0.1007 | 383 | 3.5 | 1.05 | 0.497 | 0.284 | 0.18 | 23.5 | 239 | 2280 | Therminol Reference Disk, Version 5.0
Therminol™ 75 | Solutia | Mixture of terphenyl, quaterphenyl, and phenanthrene | 80 | 385 |  | 8.2089 | 3443.0373 | 303.3212 | -4.9738 | 2294.8248 | 4.2005 | -0.80095 | 1109.219 | -8.9238e-05 | 0.13859 | 0.0024114 | 1.5434 | 185 | 343 |  |  |  | 80 | 140 | 200 | 260 | 320 | 380 | 1040 | 998 | 953 | 905 | 855 | 799 | 1.709 | 1.887 | 2.048 | 2.191 | 2.319 | 2.434 | 0.1307 | 0.1262 | 0.1213 | 0.1161 | 0.1103 | 0.1038 | 4.29 | 1.69 | 0.847 | 0.495 | 0.322 | 0.227 | 2.77 | 125 | 1480 | Therminol Reference Disk, Version 5.0
Therminol™ D-12 | Solutia | Hydrotreated heavy naphtha (petroleum) | -85 | 230 |  | 6.8095 | 1502.0865 | 190.34 | -4.2425 | 1070.6122 | -58.8354 | -0.77829 | 774.6171 | -0.00016866 | 0.11207 | 0.004052 | 2.0218 | 59 | 192 |  |  |  | -85 | -35 | 15 | 65 | 115 | 215 | 835 | 801 | 766 | 729 | 691 | 600 | 1.694 | 1.881 | 2.073 | 2.271 | 2.476 | 2.911 | 0.1244 | 0.118 | 0.1107 | 0.1027 | 0.0939 | 0.0738 | 359 | 5.63 | 1.38 | 0.664 | 0.395 | 0.174 | 0.00138 | 8.45 | 1270 | Therminol Reference Disk, Version 5.0
Therminol™ LT | Solutia | Diethyl benzene | -75 | 315 |  | 7.9345 | 2207.4431 | 255.7319 | -4.4571 | 1355.5857 | 16.3593 | -0.90647 | 880.3186 | -0.00019929 | 0.12841 | 0.0037059 | 1.7191 | 57 | 181 |  |  |  | -75 | -25 | 25 | 75 | 175 | 275 | 939 | 901 | 862 | 821 | 732 | 619 | 1.432 | 1.629 | 1.82 | 2.004 | 2.357 | 2.74 | 0.1429 | 0.1334 | 0.1237 | 0.1138 | 0.0938 | 0.0732 | 11 | 1.95 | 0.831 | 0.478 | 0.223 | 0.128 | 0.0233 | 18.2 | 5960 | Therminol Reference Disk, Version 5.0
Therminol™ VLT | Solutia | Mixture of methyl cyclohexane and trimethyl pentane | -115 | 175 |  | 6.9078 | 1331.2905 | 231.3813 | -4.8591 | 1392.5267 | 19.0588 | -0.87886 | 763.1219 | -0.00021246 | 0.10692 | 0.0042274 | 1.8664 | -6.2 | 99.2 |  |  |  | -115 | -65 | -15 | 35 | 85 | 135 | 862 | 820 | 778 | 735 | 690 | 641 | 1.374 | 1.594 | 1.808 | 2.018 | 2.225 | 2.433 | 0.1304 | 0.1208 | 0.1109 | 0.1004 | 0.0892 | 0.0771 | 45.4 | 3.56 | 1.12 | 0.547 | 0.319 | 0.202 | 0.0806 | 81.3 | 1880 | Therminol Reference Disk, Version 5.0
Therminol™ VP-1 | Solutia | Mixture of diphenyl ether and biphenyl | 12 | 400 |  | 7.1036 | 1867.1932 | 185.1089 | -4.0836 | 1380.2383 | -35.3401 | -0.92714 | 1089.4686 | -0.00015331 | 0.14195 | 0.002764 | 1.4944 | 110 | 257 |  |  |  | 12 | 72 | 132 | 192 | 252 | 372 | 1070 | 1020 | 972 | 920 | 865 | 733 | 1.523 | 1.696 | 1.864 | 2.027 | 2.186 | 2.523 | 0.137 | 0.1309 | 0.1236 | 0.115 | 0.1052 | 0.0818 | 5.48 | 1.45 | 0.693 | 0.418 | 0.284 | 0.209 | 0.694 | 142 | 5650 | Therminol Reference Disk, Version 5.0
Therminol™ VP-3 | Solutia | Mixture of cyclohexylbenzene and bicyclohexyl | 2 | 330 |  | 8.5189 | 2824.4219 | 258.0411 | -5.231 | 2426.381 | 97.6343 | -0.85238 | 959.8952 | -0.00013381 | 0.12027 | 0.0040514 | 1.5308 | 104 | 243 |  |  |  | 2 | 62 | 122 | 182 | 242 | 302 | 942 | 909 | 869 | 819 | 759 | 684 | 1.516 | 1.798 | 2.048 | 2.272 | 2.486 | 2.76 | 0.1197 | 0.112 | 0.1042 | 0.0962 | 0.088 | 0.0795 | 5.08 | 1.29 | 0.67 | 0.431 | 0.292 | 0.197 | 0.494 | 126 | 2990 | Therminol Reference Disk, Version 5.0
Therminol™ XP | Solutia | White mineral oil | -20 | 315 |  | 7.7923 | 2928.8936 | 238.1675 | -3.2691 | 948.082 | -162.9543 | -0.65886 | 891.8371 | -9.4657e-05 | 0.11761 | 0.0042291 | 1.7367 | 199 | 358 |  |  |  | -20 | 30 | 80 | 130 | 180 | 280 | 903 | 872 | 840 | 808 | 775 | 705 | 1.617 | 1.864 | 2.096 | 2.314 | 2.519 | 2.886 | 0.118 | 0.1148 | 0.1109 | 0.1065 | 0.1015 | 0.0896 | 1840 | 32.9 | 5.33 | 1.97 | 1.03 | 0.432 | 0.000742 | 0.687 | 138 | Therminol Reference Disk, Version 5.0
Water | NA | City water | 4 | 150 |  | 8.0276 | 1706.1342 | 231.4922 | -3.6338 | 544.0167 | -144.089 | -0.45804 | 1006.3465 | 0.0011752 | 0.5689 | 0.00017023 | 4.193 | 0 | 100 |  | 18.02 | 2260 | 4 | 25 | 50 | 80 | 100 | 100 | 1000 | 997.045 | 988.037 | 971.83 | 958.365 | 958.365 | 4.216 | 4.183 | 4.183 | 4.199 | 4.219 | 4.219 | 0.56422 | 0.59883 | 0.6421 | 0.66979 | 0.68018 | 0.68018 | 1.5674 | 0.8937 | 0.5494 | 0.3565 | 0.2838 | 0.2838 | 23.76 | 355.1 | 760 | 0
XCELTHERM® 445FP | Radco | Hydroprocessed napthenic mineral oil; high flash point | 20 | 288 |  | 16.783 | 15071.0082 | 735.1177 | -2.9933 | 961.1818 | -171.1277 | -0.48942 | 875.5652 | -6.2199e-05 | 0.13389 | 0.0037628 | 2.0431 | 229 | 357 | Paraffinic |  |  | 10 | 26.7 | 104.4 | 171.1 | 226.7 | 287.8 | 870.7 | 862.51 | 824.42 | 791.8 | 764.63 | 734.73 | 2.0817 | 2.1428 | 2.4358 | 2.6869 | 2.8961 | 3.1263 | 0.1333 | 0.1322 | 0.1274 | 0.1232 | 0.1198 | 0.116 | 318.94 | 87.687 | 5.306 | 1.692 | 0.931 | 0.59 | 0.001 | 1.42 | 112.1 | www.radcoind.com
XCELTHERM® 500 | Radco | Hydrogenated polyalpha olefin | -62 | 260 |  | 13.3861 | 9928.1937 | 645.8913 | -3.2591 | 832.2064 | -139.3741 | -0.61042 | 802.2908 | -5.5929e-05 | 0.13774 | 0.0041875 | 2.0762 | 163 | 500 | PAO Synthetic |  |  | -62 | -40 | -17.8 | 71.1 | 143.3 | 260 | 840.23 | 826.67 | 813.11 | 758.87 | 714.8 | 643.61 | 1.816 | 1.909 | 2.002 | 2.374 | 2.676 | 3.165 | 0.1412 | 0.14 | 0.1387 | 0.1338 | 0.1297 | 0.1232 | 3137 | 274.6 | 48.229 | 2.232 | 0.828 | 0.318 | 0.001 | 0.346 | 267 | www.radcoind.com
XCELTHERM® 600 | Radco | Hydroprocessed paraffinic white mineral oil | 50 | 343 |  | 8.2986 | 3733.1372 | 303.7075 | -3.8511 | 1092.5413 | -146.3289 | -0.6078 | 863.9763 | -8.0851e-05 | 0.13771 | 0.0034255 | 1.9233 | 193 | 301 | Paraffinic |  |  | 10 | 26.7 | 104.4 | 171.1 | 226.7 | 315 | 857.81 | 847.72 | 800.56 | 760.09 | 726.32 | 672.36 | 1.956 | 2.013 | 2.285 | 2.511 | 2.699 | 3.001 | 0.1369 | 0.1355 | 0.1293 | 0.1239 | 0.1194 | 0.1122 | 75.697 | 26.191 | 2.191 | 0.832 | 0.483 | 0.252 | 0.001 | 2.73 | 184 | www.radcoind.com
XCELTHERM® HT | Radco | Synthetic alkyl aromatic | -37 | 349 |  | 18.6859 | 22435.3789 | 1102.3712 | -3.1078 | 665.0132 | -170.7021 | -0.71955 | 1016.995 | -8.5958e-05 | 0.11911 | 0.0033129 | 1.3367 | 160 | 305 |  |  |  | -37.2 | -17.8 | 48.9 | 148.9 | 248.9 | 349 | 1043.8 | 1029.8 | 981.8 | 909.8 | 837.9 | 765.9 | 1.213 | 1.278 | 1.499 | 1.83 | 2.161 | 2.493 | 0.12 | 0.122 | 0.116 | 0.107 | 0.097 | 0.089 | 1601.8 | 115.4 | 2.246 | 0.63 | 0.314 | 0.195 | 0.01 | 5.7 | 1690 | www.radcoind.com
XCELTHERM® LV1 | Radco | Diphenyl ethane and diphenyl oxide mixture | 7 | 371 |  |  |  |  | -4.0027 | 1273.6916 | -65.5433 | -0.83461 | 1080.2295 | -0.0001521 | 0.14061 | 0.002804 | 1.5167 | 122 | 258 |  |  |  | 7.2 | 48.9 | 126.7 | 204.4 | 304.4 | 371.1 | 1074.2 | 1039.43 | 974.52 | 909.61 | 826.16 | 770.52 | 1.532 | 1.656 | 1.877 | 2.091 | 2.365 | 2.559 | 0.1372 | 0.1329 | 0.1233 | 0.112 | 0.0948 | 0.0818 | 8.416 | 2.619 | 0.872 | 0.402 | 0.226 | 0.165 | 0 | 0 | 0 | www.radcoind.com
XCELTHERM® MK1 | Radco | Diphenyl oxide and diphenyl | 15 | 400 |  | 7.117 | 1876.735 | 185.9894 | -4.1186 | 1398.0106 | -34.9854 | -0.95653 | 1092.5879 | -0.00015789 | 0.14225 | 0.0028096 | 1.4894 | 124 | 257 |  |  |  | 15.6 | 48.9 | 126.7 | 204.4 | 304.4 | 398.9 | 1068.5 | 1041.3 | 977.2 | 909.9 | 812.2 | 695.3 | 1.532 | 1.632 | 1.85 | 2.059 | 2.327 | 2.624 | 0.1371 | 0.1336 | 0.1244 | 0.1132 | 0.0957 | 0.076 | 4.961 | 2.12 | 0.73 | 0.383 | 0.216 | 0.146 | 0.134 | 204 | 8096 | 0
XCELTHERM® XT | Radco | Synthetic alkyl aromatic | -57 | 343 |  | 11.5929 | 7224.2433 | 549.2733 | -3.7834 | 1086.9427 | -92.3971 | -0.72908 | 1011.05 | -0.00015422 | 0.13666 | 0.0030904 | 1.6409 | 121 | 275 |  |  |  | -45.6 | -17.8 | 48.9 | 148.9 | 248.9 | 343.3 | 1044.16 | 1024.18 | 976.22 | 904.27 | 823.33 | 764.39 | 1.5 | 1.586 | 1.792 | 2.101 | 2.41 | 2.702 | 0.1437 | 0.1394 | 0.1291 | 0.1137 | 0.0983 | 0.0837 | 114.95 | 17.938 | 2.264 | 0.615 | 0.282 | 0.181 | 0.01 | 17.6 | 3156 | www.radcoind.com

## Yaws Data
Use this worksheet to capture parameters from Yaws publications, such as "Yaws' Handbook of Thermodynamic and Physical Properties of Chemical Compounds", then copy to the Fluid Data sheet for entry into the database.
|  | Heat Capacity of Liquid | [5 empty] | Density of Liquid | [5 empty] | Liquid Viscosity | [6 empty] | Liquid thermal conductivity |  |  |  |  | Vapor Pressure
|  | Cp = A + BT + CT2 + DT3 | [5 empty] | density = A B^(-(1-T/Tc)^n) | [5 empty] | log10(cP) = a + B/T + CT + DT2 | [6 empty] | k = A + BT + CT^2, W/(m-K) |  |  |  |  | log10(mm Hg) = A + B/T + ClogT + DT + ET^2 | [6 empty] | Heat Vap | FP | BP
|  | A | B | C | D | Temp | J/mol-K | A | B | n | Tc | Temp | g/cc | A | B | C | D | Temp | cP | MW | A | B | C | Temp | W/m-K | A | B | C | D | E | Temp | mm Hg | kJ/kg | C | C
Butane, n | C4H10 | 62.873 | 0.58913 | -0.0023588 | 4.2257e-06 | 298 | 140.7901 | 0.2283 | 0.2724 | 0.2863 | 425.18 | 25 | 0.573 | -6.859 | 673.93 | 0.022 | -3.0686e-05 | 298.15 | 0.17096 | 58.123 | 0.2384 | -0.00037626 | -2.5291e-07 | 298.15 | 0.10374 | 27.044 | -1904.9 | -7.1805 | -6.6845e-11 | 4.219e-06 | 298.15 | 1829.3476 | 386.116 | -59.4444 | -0.44444
Pentane | C5H12 | 80.641 | 0.62195 | -0.0022682 | 3.7423e-06 | 298.15 | 163.6317 | 0.2314 | 0.2692 | 0.2822 | 469.65 | 25 | 0.62124 | -7.1711 | 747.36 | 0.0217 | -2.7176e-05 | 298.15 | 0.24527 | 72.15 | 0.1877 | -3.7842e-06 | -4.3481e-07 | 298.15 | 0.14792 | 33.324 | -2422.7 | -9.2354 | 9.0199e-11 | 4.105e-06 | 298.15 | 513.732 | 357.5062 | -49.4444 | 36.0556
Hexane | C6H14 | 78.848 | 0.88729 | -0.0029482 | 4.1999e-06 | 298.15 | 192.6303 | 0.2324 | 0.265 | 0.2781 | 507.43 | 25 | 0.65626 | -5.0715 | 655.36 | 0.0123 | -1.5042e-05 | 298.15 | 0.28622 | 86.177 | 0.2096 | -0.00022594 | -2.3421e-07 | 298.15 | 0.12142 | 69.738 | -3627.8 | -23.927 | 0.01281 | -1.6844e-13 | 298.15 | 152.6859 | 334.944 | -21.6667 | 68.7778
Octane | C8H18 | 82.736 | 1.3043 | -0.0038254 | 4.6459e-06 | 298.15 | 254.6931 | 0.2281 | 0.2548 | 0.2694 | 568.83 | 25 | 0.69864 | -5.9245 | 888.09 | 0.013 | -1.3596e-05 | 298.15 | 0.52665 | 114.231 | 0.1996 | -0.00017706 | -1.9969e-07 | 298.15 | 0.12906 | 29.095 | -3011.4 | -7.2653 | -2.2696e-11 | 1.468e-06 | 298.15 | 14.0507 | 302.38 | 13.3333 | 125.6667
|  |  |  | Fluid Name: |  | Octane
Manufacturer:
|  |  |  | Description: |  | pure component |  |  | Heat Vap | 302.38
|  |  |  | Operating range: |  |  | °C minimum |  | FP | 13.3333
[7 empty] | °C maximum |  | BP | 125.6667
|  |  |  | Source: |  | Yaw's Handbook, 2003 |  |  | Mol Wt | 114.231
[6 empty] | Liquid |  | Thermal |  | Vapor
[5 empty] | Temp. | Density | Sp. Heat | Conduct. | Visc. | Pressure
|  |  |  | K | °C | kg/cu.m. | KJ/kg-°K | W/m-°K | cP | mm Hg
|  | Row | 4 | 253.15 | -20 | 732.5191 | 2.1285 | 0.14198 | 1.0076 | 0.67936
|  |  |  | 293.15 | 20 | 702.5186 | 2.2182 | 0.13053 | 0.55915 | 10.5791
|  |  |  | 333.15 | 60 | 670.5874 | 2.3152 | 0.11845 | 0.36575 | 77.8082
|  |  |  | 373.15 | 100 | 636.161 | 2.4352 | 0.10573 | 0.25901 | 349.6937
|  |  |  | 393.15 | 120 | 617.7531 | 2.5086 | 0.099123 | 0.22073 | 648.6166
|  |  |  | 413.15 | 140 | 598.3474 | 2.5937 | 0.092362 | 0.18848 | 1121.7379