## Home
Chapter 6: Fans, Blowers, and Compressors
Rules of Thumb for Chemical Engineers, 5th Edition
by Stephen Hall
This Excel workbook includes Visual Basic for Application function subroutines.
Macros must be enabled for them to work.
The following Text Boxes contain the syntax for the functions.
Copy them to the worksheet where you want to use the functions for ready reference.
Function ZSI(P, T, Pc, Tc)
' calculates compressibility factor, Z, using SI units
' P = gas pressure, kPa
' T = gas temperature, C
' Pc = gas pseudo-critical pressure, atm
' Tc = gas pseudo-critical temperature, C
Function ZUS(P, T, Pc, Tc)
' calculates compressibility factor, Z, using US units
' P = gas pressure, psia
' T = gas temperature, F
' Pc = gas pseudo-critical pressure, psia
' Tc = gas pseudo-critical temperature, F

## Power - Recip
Inputs
| Fluid |  | Air |  | Air | Air
| flow rate | m3/h at inlet conditions | 500 | cfm at inlet conditions | 294 | 422
| Inlet pressure | kPa-absolute | 101.3 | psia | 14.7 | 14.7
| Inlet temperature | C | 25 | F | 77 | 77
| Discharge pressure | kPa-absolute | 900 | psia | 130.5 | 140
| Number of stages |  | 2 |  | 2 | 2
Intermediate Lookup Values and Calculations
| Overall compression ratio |  | 8.8845 |  | 8.8776 | 9.5238
| Compression ratio per stage |  | 2.9807 |  | 2.9795 | 3.0861
| Gas constant | R | 8314.47 |  | 10.73 | 10.73
| MW |  | 29 |  | 29 | 29
| heat capacity ratio | k | 1.4 |  | 1.4 | 1.4
| density at inlet | kg/m3 | 1.1851 | lb/ft3 | 0.073998 | 0.073998 | density = (P M) / (R T)
| mass flow rate | kg/s | 0.16459 | lb/s | 0.36259 | 0.52046
Outputs
Reciprocating Compressor - GPSA Shortcut Formula
| C |  | 0.013 |  | 0.03 | 0.03
| F |  | 1.08 |  | 1.08 | 1.08
| R |  | 2.9807 |  | 2.9795 | 3.0861
| N |  | 2 |  | 2 | 2
| Q | m3/h at 100 kPa | 506.5 | cfm at 14.5 psia | 298.0552 | 427.8207
| Adjustment for high speed compressor (see text) |  | 0.1 |  | 0.1 | 0.2
| Brake Power (shaft power) | kW | 46.6322 | hp | 63.3011 | 102.6652
|  |  |  | kw | 47.2226 | 76.5883
|  |  |  | motor efficiency |  | 0.949
80.7042
Problem Statement:
Calculate the shaft (brake) power of a reciprocating compressor
See Text for values

## Power - Centrif
Inputs
| Fluid |  | Air |  |  | Air
| flow rate | m3/h at inlet conditions | 500 | 500 | cfm at inlet conditions | 294
| Inlet pressure | kPa-absolute | 101.3 | 206.8043 | psia | 14.7
| Inlet temperature | C | 25 | 40.18 | F | 77
| Discharge pressure | kPa-absolute | 900 | 900 | psia | 130.5
| Number of stages |  | 2 | 3 |  | 2
| Intercooler temperature approach | C | 5 | 5 | F | 10
| Polytropic Efficiency |  | 0.7 | 0.7 |  | 0.7
Intermediate Lookup Values and Calculations
| Overall compression ratio |  | 8.8845 | 4.3519 |  | 8.8776
| Compression ratio per stage |  | 2.9807 | 1.6327 |  | 2.9795
| Gas constant | R | 8314.47 | 8314.47 |  | 10.73
| MW |  | 29 | 45.5 |  | 29
| Critical pressure | atm | 39 | 41.53 | psia | 573
| Critical temperature | C | -140 | 101.89 | F | -220
| heat capacity ratio | k | 1.4 | 1.4 |  | 1.4
| density at inlet | kg/m3 | 1.1851 | 3.6119 | lb/ft3 | 0.073998
| mass flow rate | kg/s | 0.16459 | 0.50165 | lb/s | 0.36259
Outputs
Stage 1
Compressibility factor using Redlich-Kwong EOS
| Inlet compressibility | Z | #VALUE! | #VALUE! | Z | #VALUE!
| Discharge compressibility |  | #VALUE! | #VALUE! |  | #VALUE!
| Average compressibility |  | #VALUE! | #VALUE! |  | #VALUE!
Polytropic compression
| Polytropic exponent | n | 1.6897 | 1.6897 | n | 1.6897
| Stage discharge pressure | kPa-absolute | 301.9437 | 337.64 | psia | 43.799
| Discharge temperature | C | 192.4719 | 109.5845 | F | 378.5008
| Polytropic head | kN-m/kg | #VALUE! | 31.0726 | ft-lbf/lbm | #VALUE!
| Polytropic gas power | kW | #VALUE! | 22.268 | hp | #VALUE!
Stage 2
Compressibility factor using Redlich-Kwong EOS
| Inlet compressibility | Z | #VALUE! | #VALUE! | Z | #VALUE!
| Discharge compressibility |  | #VALUE! | #VALUE! |  | #VALUE!
| Average compressibility |  | #VALUE! | #VALUE! |  | #VALUE!
Polytropic compression
| Polytropic exponent | n | 1.6897 | 1.6897 | n | 1.6897
| Stage inlet temperature | C | 30 | 45.18 | F | 87
| Stage inlet density | kg/m3 | 3.474 | 5.8043 | lb/ft3 | 0.21645
| Stage discharge pressure | kPa-absolute | 900 | 551.2495 | psia | 130.5
| Discharge temperature | C | 200.2804 | 115.692 | F | 394.1154
| Polytropic head | kN-m/kg | #VALUE! | 31.5684 | ft-lbf/lbm | #VALUE!
| Polytropic gas power | kW | #VALUE! | 22.6233 | hp | #VALUE!
Stage 3
Compressibility factor using Redlich-Kwong EOS
| Inlet compressibility | Z | #VALUE! | #VALUE! |  | #VALUE!
| Discharge compressibility |  | #VALUE! | #VALUE! |  | #VALUE!
| Average compressibility |  | #VALUE! | #VALUE! |  | #VALUE!
Polytropic compression
| Polytropic exponent | n | 1.6897 | 1.6897 | n | 1.6897
| Stage inlet temperature | C | 30 | 45.18 | F | 87
| Stage inlet density | kg/m3 | 10.355 | 9.4765 | lb/ft3 | 0.64491
| Stage discharge pressure | kPa-absolute | 2682.6193 | 900 | psia | 388.8276
| Discharge temperature | C | 200.2804 | 115.692 | F | 394.1154
| Polytropic head | kN-m/kg | #VALUE! | 31.5684 | ft-lbf/lbm | #VALUE!
| Polytropic gas power | kW | 0 | 22.6233 | hp | 0
| Total gas power | kW | #VALUE! | 67.5146 | hp | #VALUE!
| Add for mechanical losses | kW | #VALUE! | 5.3921 | hp | #VALUE!
| Brake power (shaft power) | kW | #VALUE! | 72.9067 | hp | #VALUE!
Problem Statement:
Calculate the hydraulic and shaft (brake) power of a compressor

## P-E Diagram Air
Inputs
| Fluid |  |  |  | Air
| flow rate |  | m3/h at inlet conditions |  | 500
| Inlet pressure |  | kPa-absolute |  | 101.5
| Inlet temperature |  | C |  | 25
| Discharge pressure |  | kPa-absolute |  | 900
| Number of stages |  |  |  | 2
| Intercooler temperature approach |  | C |  | 5
| Isentropic Efficiency |  |  |  | 0.8
Intermediate Calculation
| Overall compression ratio |  |  |  | 8.867
| Compression ratio per stage |  |  |  | 2.9778
| Density |  | kg/m3 |  | 1.1875
Results
| Enthalpy of Compression |  | kJ/kg |  | 291.5182
| Work |  | kJ/h |  | 173083.1587
|  |  | kW |  | 48.0787
| Mechanical losses in the compressor |  |  |  | 4.7074
| Shaft power |  | kW |  | 52.7861
Stage-by-Stage Calculations by Interpolating the P-E Data | [9 empty] | Entry Point into Table and Interpolation Ratio |  |  |  |  | Interpolation of the Enthalpy Data Table
|  | Point | Pressure | Enthalpy | Temperature | Entropy | Comment |  |  | Pressure | Interpolation | Temperature | Interpolation |  | Compression enthalpy
|  | 1 | 1.015 | 298.4323 | 25 | 6.8603 | Inlet conditions |  |  | 1 | 0.0092508
| Stage 1 | 2 | 3.0224 | 417.7757 | 143.3157 | 6.8805 | Compress with constant entropy |  |  | 1 | 0.68723
|  | 3 | 3.0224 | 447.6116 | 177.2486 |  | Apply isentropic compression efficiency |  |  |  |  | 8 | 0.50399 |  | 149.1793
|  | 4 | 3.0224 | 302.8654 | 30 | 6.5613 | Cool with intercooler |  |  | 1 | 0.68723
| Stage 2 | 5 | 9 | 416.7364 | 142.87 | 6.5644 | Compress with constant entropy |  |  | 2 | 0.848
|  | 6 | 9 | 445.2042 | 174.8319 |  | Apply isentropic compression efficiency |  |  |  |  | 8 | 0.47982 |  | 142.3388
|  | 7 | 9 | 301.671 | 30 | 6.2446 | Cool with intercooler |  |  | 2 | 0.848
| Stage 3 | 8 | 26.7998 | 393.4406 | 121.0918 | 6.1953 | Compress with constant entropy |  |  | 2 | 2.4222
|  | 9 | 26.7998 | 416.383 | 144.8388 |  | Apply isentropic compression efficiency |  |  |  |  | 8 | 0.17989 |  | 0
|  | 10 | 26.7998 | 297.4735 | 30 | 5.9187 | Cool with aftercooler |  |  | 4 | 0.42222
Data | Source: Perry's Chemical Engineers' Handbook, 6th Edition, Table 3-212
Interpolation
Fluid: | Air
[21 empty] | Constant Temperature | [6 empty] | Constant Entropy
Temperature | deg K | 200 | 220 | 240 | 260 | 280 | 300 | 350 | 400 | 500 | 600 | 800 | 1000 | 1200 | 1400 | 1600 | 1800 | 2000 | 2500 |  | 298.15 | 416.4657 | 303.15 | 416.02 | 303.15 | 394.2418 | 303.15 | 6.8603 | 6.8805 | 6.5613 | 6.5644 | 6.2446 | 6.1953
| Pressure | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy |  | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy | Enthalpy
| bar | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg |  | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg | kJ/kg
| 1 | 199.7 | 219.8 | 239.9 | 260 | 280.2 | 300.3 | 350.7 | 401.2 | 503.4 | 607.5 | 822.5 | 1046.8 | 1278 | 1515 | 1764 | 2017 | 2279 | 3011 |  | 298.4407 | 418.028 | 303.4752 | 417.5724 | 303.4752 | 395.3842 | 303.4752 | 297.1877 | 303.3782 | 220.3228 | 221.0275 | #N/A | #N/A
| 5 | 197.7 | 218.1 | 238.5 | 258.8 | 279.1 | 299.4 | 350 | 400.8 | 503.2 | 607.4 | 822.6 | 1046.9 | 1279 | 1516 | 1764 | 2017 | 2278 | 2981 |  | 297.5222 | 417.6609 | 302.5878 | 417.2044 | 302.5878 | 394.9497 | 302.5878 | 473.3814 | 482.3921 | 349.4485 | 350.5171 | 254.4914 | 242.2896
| 10 | 195.2 | 216.1 | 236.7 | 257.3 | 277.8 | 298.3 | 349.2 | 400.2 | 502.9 | 607.3 | 822.7 | 1047.2 | 1279 | 1516 | 1765 | 2018 | 2279 | 2974 |  | 296.4038 | 417.1103 | 301.5067 | 416.6525 | 301.5067 | 394.3267 | 301.5067 | 576.1536 | 587.226 | 428.9064 | 430.284 | 311.4613 | 295.7544
| 20 | 190.1 | 211.9 | 233.2 | 254.3 | 275.2 | 296 | 347.7 | 399.1 | 502.4 | 607.2 | 823 | 1047.7 | 1280 | 1517 | 1766 | 2019 | 2279 | 2970 |  | 294.076 | 416.1091 | 299.2571 | 415.6486 | 299.2571 | 393.1806 | 299.2571 | 707.3394 | 721.322 | 524.4769 | 526.1266 | 380.1892 | 361.6973
| 40 | 179.7 | 203.5 | 226.3 | 248.5 | 270.2 | 291.7 | 344.6 | 397 | 501.5 | 606.9 | 823.7 | 1048.8 | 1281 | 1519 | 1768 | 2021 | 2281 | 2969 |  | 289.7113 | 414.2067 | 295.0327 | 413.7409 | 295.0327 | 390.9654 | 295.0327 | 854.4749 | 872.5465 | 639.1683 | 641.319 | 466.3358 | 444.2303
| 60 | 163.9 | 191.1 | 216.1 | 240 | 263.1 | 285.6 | 340.4 | 394 | 500.6 | 606.8 | 824.3 | 1050 | 1283 | 1521 | 1770 | 2023 | 2284 | 2969 |  | 283.5188 | 411.5525 | 289.0524 | 411.0773 | 289.0524 | 387.8272 | 289.0524 | 960.7194 | 978.7673 | 722.0254 | 724.1762 | 523.9178 | 497.5643
| 80 | 158.7 | 187.1 | 212.9 | 237.3 | 260.8 | 283.7 | 339 | 393.1 | 499.8 | 606.7 | 825.1 | 1051.1 | 1284 | 1522 | 1772 | 2025 | 2285 | 2971 |  | 281.5817 | 410.6689 | 287.1839 | 410.1933 | 287.1839 | 386.8697 | 287.1839 | 1036.1964 | 1054.9086 | 781.3425 | 783.4953 | 570.2968 | 543.277
| 100 | 148.8 | 179.4 | 206.7 | 232.2 | 256.4 | 279.9 | 336.5 | 391.3 | 499 | 606.6 | 825.8 | 1052.4 | 1286 | 1524 | 1774 | 2027 | 2288 | 2972 |  | 277.7262 | 409.0336 | 283.4658 | 408.5535 | 283.4658 | 384.989 | 283.4658 | 1105.6386 | 1127.8427 | 827.8501 | 830.6134 | 607.0145 | 579.869
| 150 | 129.2 | 163.2 | 193.4 | 221 | 247 | 271.8 | 330.9 | 387.5 | 497.5 | 606.6 | 827.8 | 1055.5 | 1290 | 1529 | 1779 | 2033 | 2294 | 2977 |  | 269.506 | 405.6123 | 275.5233 | 405.122 | 275.5233 | 380.9818 | 275.5233 | 1239.7046 | 1261.8895 | 937.4267 | 940.1925 | 692.5728 | 658.2884
| 200 | 117.6 | 152.2 | 183.6 | 212.5 | 239.6 | 265.5 | 326.5 | 384.5 | 496.6 | 607 | 829.9 | 1058.7 | 1294 | 1533 | 1783 | 2038 | 2299 | 2982 |  | 263.1042 | 402.9581 | 269.343 | 402.4584 | 269.343 | 377.8205 | 269.343 | 1342.9706 | 1368.725 | 1016.7882 | 1019.5565 | 754.3896 | 720.0576
| 250 | 111.7 | 145.6 | 177.1 | 206.6 | 234.3 | 260.8 | 323.2 | 382.3 | 496 | 607.6 | 832.2 | 1062 | 1298 | 1538 | 1789 | 2043 | 2304 | 2988 |  | 258.3487 | 401.0215 | 264.7312 | 400.5147 | 264.7312 | 375.4938 | 264.7312 | 1430.5979 | 1456.4601 | 1083.1729 | 1086.5596 | 803.4092 | 769.1367
| 300 | 109 | 142 | 173.2 | 202.7 | 230.8 | 257.7 | 320.9 | 380.9 | 495.9 | 608.5 | 834.5 | 1065.3 | 1302 | 1542 | 1794 | 2049 | 2310 | 2993 |  | 255.2117 | 399.8356 | 261.6816 | 399.323 | 261.6816 | 373.9902 | 261.6816 | 1502.8288 | 1528.5534 | 1145.986 | 1149.3827 | 847.5569 | 810.3012
| 400 | 108.5 | 140.1 | 170.5 | 199.7 | 227.8 | 254.8 | 319.1 | 380 | 496.8 | 611 | 839.4 | 1072 | 1310 | 1552 | 1804 | 2059 | 2321 | 3004 |  | 252.3025 | 399.232 | 258.8509 | 398.7113 | 258.8509 | 372.9865 | 258.8509 | 1632.3878 | 1663.3514 | 1247.8007 | 1251.1846 | 931.538 | 887.2742
| 500 | 111.4 | 142 | 171.7 | 200.5 | 228.4 | 255.4 | 319.9 | 381.3 | 499.1 | 614.3 | 844.6 | 1078.8 | 1318 | 1561 | 1814 | 2070 | 2332 | 3015 |  | 252.9025 | 400.6966 | 259.4635 | 400.1715 | 259.4635 | 374.229 | 259.4635 | 1741.9812 | 1773.0677 | 1332.2135 | 1336.0981 | 999.4732 | 955.2464
| 600 | 116 | 146.1 | 175.3 | 203.6 | 231.2 | 258.1 | 322.6 | 384.2 | 502.6 | 618.5 | 850.1 | 1085.5 | 1326 | 1570 | 1824 | 2080 | 2343 | 3026 |  | 255.6118 | 403.6954 | 262.1635 | 403.1676 | 262.1635 | 377.1059 | 262.1635 | 1834.7077 | 1868.8709 | 1408.9461 | 1412.8067 | 1056.4962 | 1012.3809
| 800 |  | 157.4 | 185.9 | 213.7 | 240.3 | 267.3 | 331.6 | 393.8 | 512.3 | 625.8 | 862 | 1099.3 | 1341 | 1588 | 1844 | 2101 | 2365 | 3049 |  | 264.8025 | 413.3119 | 271.3509 | 412.7837 | 271.3509 | 386.6368 | 271.3509 | 1998.3959 | 2032.4669 | 1533.4715 | 1537.3203 | 1196.1545 | 1152.1956
| 1000 |  |  |  | 226.4 | 253.2 | 279.5 | 343.4 | 405.1 | 524.4 | 641.2 | 875.1 | 1113.3 | 1356 | 1606 | 1863 | 2121 | 2386 | 3071 |  | 277.0673 | 424.7436 | 283.5257 | 424.2118 | 283.5257 | 397.9944 | 283.5257 | 2129.2281 | 2167.6454 | 1640.9283 | 1645.7632 | 1254.9795 | 1201.096
Interpolated Enthalpy at stage discharge pressures
Stage 1 | 3.0224 | 198.3255 | 218.6317 | 238.9379 | 259.1753 | 279.444 | 299.6815 | 350.2189 | 400.9251 | 503.2626 | 607.4313 | 822.5687 | 1046.8687 | 1278.6872 | 1515.6872 | 1764 | 2017 | 2278.3128 | 2990.3831
Stage 2 | 9 | 195.58 | 216.404 | 236.9736 | 257.528 | 277.9976 | 298.4672 | 349.3216 | 400.2912 | 502.9456 | 607.3152 | 822.6848 | 1047.1544 | 1279 | 1516 | 1764.848 | 2017.848 | 2278.848 | 2975.064
Stage 3 | 26.7998 | 191.6445 | 213.2556 | 234.14 | 255.1667 | 275.9511 | 296.7356 | 348.0622 | 399.3467 | 502.4733 | 607.1578 | 822.8422 | 1047.6267 | 1279 | 1516 | 1766.4222 | 2019.4222 | 2280.4222 | 2964.0445
| Pressure | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy |  | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy | Entropy |  | Temperature
| bar | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) |  | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | kJ/(kg-C) | deg K | deg K | deg K | deg K | deg K | deg K
| 1 | 6.463 | 6.559 | 6.647 | 6.727 | 6.802 | 6.871 | 7.026 | 7.161 | 7.389 | 7.579 | 7.888 | 8.138 | 8.349 | 8.531 | 8.695 | 8.695 | 8.983 | 9.308 |  | 6.8646 | 7.1985 | 6.8808 | 7.1975 | 6.8808 | 7.1455 | 6.8808 | 296.9032 | 303.0538 | 220.5202 | 221.2214 | #N/A | #N/A
| 5 | 5.994 | 6.092 | 6.18 | 6.262 | 6.337 | 6.406 | 6.563 | 6.698 | 6.927 | 7.116 | 7.426 | 7.676 | 7.887 | 8.069 | 8.233 | 8.233 | 8.52 | 8.832 |  | 6.3996 | 6.7357 | 6.4159 | 6.7347 | 6.4159 | 6.6825 | 6.4159 | 470.8803 | 479.6798 | 349.4551 | 350.509 | 255.755 | 243.7336
| 10 | 5.786 | 5.885 | 5.975 | 6.058 | 6.134 | 6.204 | 6.361 | 6.497 | 6.727 | 6.917 | 7.226 | 7.477 | 7.688 | 7.87 | 8.034 | 8.034 | 8.321 | 8.63 |  | 6.1975 | 6.5349 | 6.2139 | 6.5338 | 6.2139 | 6.4813 | 6.2139 | 570.1662 | 580.772 | 427.9517 | 429.2931 | 312.9285 | 297.5165
| 20 | 5.568 | 5.672 | 5.765 | 5.849 | 5.927 | 5.998 | 6.158 | 6.295 | 6.52 | 6.716 | 7.027 | 7.277 | 7.489 | 7.671 | 7.835 | 7.835 | 8.121 | 8.428 |  | 5.9914 | 6.332 | 6.0081 | 6.331 | 6.0081 | 6.2792 | 6.0081 | 692.8076 | 705.7664 | 521.0658 | 522.6399 | 381.6042 | 363.616
| 40 | 5.33 | 5.444 | 5.543 | 5.632 | 5.712 | 5.786 | 5.95 | 6.09 | 6.323 | 6.515 | 6.826 | 7.077 | 7.289 | 7.473 | 7.636 | 7.636 | 7.922 | 8.229 |  | 5.7792 | 6.1284 | 5.7963 | 6.1273 | 5.7963 | 6.0739 | 5.7963 | 827.3433 | 843.3999 | 629.7678 | 631.7519 | 466.3501 | 445.1965
| 60 | 5.174 | 5.298 | 5.404 | 5.497 | 5.581 | 5.657 | 5.824 | 5.967 | 6.202 | 6.396 | 6.708 | 6.96 | 7.172 | 7.355 | 7.52 | 7.52 | 7.806 | 8.112 |  | 5.65 | 6.0057 | 5.6675 | 6.0046 | 5.6675 | 5.9505 | 5.6675 | 920.8856 | 936.8784 | 705.9544 | 707.9322 | 521.9565 | 497.1523
| 80 | 5.051 | 5.186 | 5.299 | 5.396 | 5.484 | 5.562 | 5.733 | 5.878 | 6.116 | 6.311 | 6.624 | 6.877 | 7.089 | 7.273 | 7.437 | 7.437 | 7.723 | 8.029 |  | 5.5548 | 5.9172 | 5.5728 | 5.9161 | 5.5728 | 5.8613 | 5.5728 | 986.811 | 1003.2706 | 759.929 | 761.9004 | 565.9465 | 540.6707
| 100 | 4.949 | 5.095 | 5.214 | 5.315 | 5.406 | 5.486 | 5.661 | 5.807 | 6.048 | 6.244 | 6.559 | 6.812 | 7.024 | 7.208 | 7.373 | 7.373 | 7.659 | 7.964 |  | 5.4786 | 5.8467 | 5.497 | 5.8456 | 5.497 | 5.7902 | 5.497 | 1045.581 | 1064.5913 | 801.8094 | 804.2484 | 600.3782 | 575.1571
| 150 | 4.757 | 4.919 | 5.051 | 5.161 | 5.257 | 5.343 | 5.525 | 5.677 | 5.922 | 6.121 | 6.439 | 6.693 | 6.906 | 7.092 | 7.256 | 7.256 | 7.543 | 7.848 |  | 5.335 | 5.7173 | 5.3545 | 5.7162 | 5.3545 | 5.6595 | 5.3545 | 1157.1041 | 1176.0252 | 896.2905 | 898.7198 | 677.7331 | 646.7345
| 200 | 4.631 | 4.796 | 4.932 | 5.048 | 5.149 | 5.238 | 5.426 | 5.581 | 5.831 | 6.033 | 6.353 | 6.608 | 6.822 | 7.009 | 7.173 | 7.173 | 7.46 | 7.765 |  | 5.2298 | 5.6222 | 5.2498 | 5.621 | 5.2498 | 5.5631 | 5.2498 | 1240.9795 | 1262.5314 | 963.3638 | 965.7837 | 732.2473 | 701.4424
| 250 | 4.544 | 4.706 | 4.843 | 4.961 | 5.064 | 5.155 | 5.348 | 5.506 | 5.76 | 5.963 | 6.286 | 6.542 | 6.757 | 6.944 | 7.108 | 7.108 | 7.396 | 7.701 |  | 5.1466 | 5.5478 | 5.1672 | 5.5467 | 5.1672 | 5.4878 | 5.1672 | 1310.4983 | 1332.0501 | 1017.9432 | 1020.8132 | 774.3626 | 743.8439
| 300 | 4.48 | 4.637 | 4.773 | 4.891 | 4.995 | 5.088 | 5.283 | 5.443 | 5.7 | 5.906 | 6.23 | 6.488 | 6.703 | 6.891 | 7.056 | 7.206 | 7.344 | 7.648 |  | 5.0794 | 5.4853 | 5.1003 | 5.4842 | 5.1003 | 5.4246 | 5.1003 | 1367.3573 | 1388.7945 | 1068.1757 | 1071.0458 | 811.3144 | 778.5851
| 400 | 4.386 | 4.537 | 4.669 | 4.786 | 4.89 | 4.983 | 5.181 | 5.344 | 5.605 | 5.813 | 6.142 | 6.401 | 6.618 | 6.808 | 6.972 | 7.123 | 7.261 | 7.566 |  | 4.9744 | 5.387 | 4.9955 | 5.3858 | 4.9955 | 5.3252 | 4.9955 | 1463.7998 | 1488.3742 | 1147.7317 | 1150.5753 | 879.2244 | 841.1644
| 500 | 4.317 | 4.463 | 4.593 | 4.708 | 4.811 | 4.905 | 5.103 | 5.267 | 5.531 | 5.741 | 6.072 | 6.333 | 6.55 | 6.743 | 6.907 | 7.058 | 7.196 | 7.501 |  | 4.8963 | 5.3105 | 4.9175 | 5.3093 | 4.9175 | 5.2481 | 4.9175 | 1543.0681 | 1567.6425 | 1211.6983 | 1214.8955 | 932.2572 | 894.4888
| 600 | 2.263 | 4.406 | 4.533 | 4.646 | 4.749 | 4.842 | 5.041 | 5.205 | 5.47 | 5.681 | 6.014 | 6.277 | 6.495 | 6.69 | 6.854 | 7.005 | 7.144 | 7.449 |  | 4.8334 | 5.2486 | 4.8545 | 5.2475 | 4.8545 | 5.1861 | 4.8545 | 1608.3654 | 1635.0554 | 1267.9886 | 1271.153 | 975.3579 | 937.8767
| 800 |  | 4.318 | 4.442 | 4.553 | 4.653 | 4.745 | 4.943 | 5.108 | 5.374 | 5.586 | 5.922 | 6.136 | 6.407 | 6.605 | 6.769 | 6.921 | 7.06 | 7.366 |  | 4.7365 | 5.1518 | 4.7575 | 5.1506 | 4.7575 | 5.089 | 4.7575 | 1720.1525 | 1746.6669 | 1355.8474 | 1358.9638 | 1080.1444 | 1043.7696
| 1000 |  |  |  | 4.482 | 4.582 | 4.672 | 4.869 | 5.034 | 5.3 | 5.513 | 5.85 | 6.115 | 6.337 | 6.539 | 6.703 | 6.856 | 6.995 | 7.302 |  | 4.6637 | 5.0778 | 4.6844 | 5.0766 | 4.6844 | 5.015 | 4.6844 | 1806.2099 | 1835.2041 | 1427.1816 | 1430.9441 | 1116.7528 | 1072.3494
[20 empty] | Temperature | 5 | 8 | 6 | 8 | 6 | 7 | 6
[20 empty] | Interpolation | 0.9075 | 0.16466 | 0.063 | 0.1602 | 0.063 | 0.88484 | 0.063
Add these values together for total enthalpy of compression
Problem Statement:
Calculate the shaft (brake) power of a compressor by interpolating the Pressure-Enthalpy data table
The data tables give enthalpy and entropy at pressure and temperature combinations. Values are in RED text; these are the values to change to enter data for a different ccompound.
Beginning with the compressor inlet pressure and temperature, the P-E tables are interpolated to:
a) follow a constant entropy path from inlet conditions to the stage discharge pressure
b) increase the temperature, at constant pressure, by applying the isentropic efficiency to the amount of enthalpy gain in (a)
c) capture the enthalpy change for the stage
d) cool the gas to a temperature near the inlet temperature; this is performed at constant pressure
e) look up the new enthalpy
f) repeat for stages 2 and 3
The x and y scales on the chart adjust automatically to fit the pressure range entered in the Input section. To see the chart expanded to encompass the full range of enthalpy data, click the "Reset Chart Area" button.
Result
Reset Chart Area