## Data Sheet
PipeCapacity.xls
This spreadsheet computes capacity of gas pipelines.
Input Data:
| Pipe I.D.: |  |  | 12.09 | in.
| Pipe roughness: |  |  | 0.0006 | in.
| Pipeline length: |  |  | 200 | miles
| Average temperature: |  |  | 80 | oF
| Base temperature: |  |  | 60 | oF
| Base pressure: |  |  | 14.7 | psia
| Inlet pressure: |  |  | 600 | psia
| Outlet pressure: |  |  | 200 | psia
| Gas properties: |  |  |  |  | a0 | -2.462
|  | Gas specific gravity: |  | 0.7 | air = 1 | a1 | 2.97
|  | Mole fraction of N2: |  | 0 |  | a2 | -0.2862
|  | Mole fraction of CO2: |  | 0 |  | a3 | 0.008054
|  | Mole fraction of H2S: |  | 0 |  | a4 | 2.808
[6 empty] | a5 | -3.498
[6 empty] | a6 | 0.3603
Calculated Parameter Values: | [5 empty] | a7 | -0.01044
[6 empty] | a8 | -0.7933
| Pseudocritical pressure: |  |  | 668 | psia | a9 | 1.396
| Pseudocritical temperature: |  |  | 389.14 | R | a10 | -0.1491
| Uncorrected gas viscosity at 14.7 psia: |  |  | 0.010079 | cp | a11 | 0.00441
| N2 correction for gas viscosity at 14.7 psia: |  |  | 0 | cp | a12 | 0.08393
| CO2 correction for gas viscosity at 14.7 psia: |  |  | 0 | cp | a13 | -0.1864
| H2S correction for gas viscosity at 14.7 psia: |  |  | 0 | cp | a14 | 0.02033
| Corrected gas viscosity at 14.7 psia (m1): |  |  | 0.010079 | cp | a15 | -0.0006095
| Gas viscosity: |  |  | 0.0098992 | cp
| Pseudo-reduced temperature: |  |  | 1.3363 |  | A = | 0.31476
| Average pressure (psia): |  |  | 400 | psia | C = | 0.091713
| Pseudo-reduced pressure: |  |  | 0.5988 |  | D = | 0.95835
| Average z-factor: |  |  | 0.91878 |  | B = | 0.22365
| Pipe relative roughness: |  |  | 4.9628e-05 |  | ln (mg/m1*Tpr) = | 0.27184
Solution:
A) Use Reynolds number-dependent friction factor:
| Pipeline flow capacity |  | = | 1188000.13 | cfh
| Reynolds number = |  |  | 3335270.1249
| Friction factor = |  |  | 0.011431
| Objective function = |  |  | -2.5638e-05
B) Use Weymouth Equation:
| Pipeline flow capacity = |  |  | 1076034.7402 | cfh
Instructions: 1. Update input data in blue; 2. Run Macro Solution; 3. View results.